## component_list
Description: | This file lists the instances of various component types within the system. Component design level 0.35g.
Note: | Cost fractions define economic value of the individual component relative to the cost of entire system. Data includes a 4% allowance for components not included in the model.
component_id | component_type | component_class | cost_fraction | node_type | node_cluster | op_capacity
coal_supply | SYSTEM_INPUT | Coal Delivery and Storage | 0 | supply | INPUT | 1
unloader_1 | Unloader | Coal Delivery and Storage | 0.025954 | transshipment | Fuel Supply | 1
unloader_2 | Unloader | Coal Delivery and Storage | 0.025954 | transshipment | Fuel Supply | 1
coal_yard | Coal Yard | Coal Delivery and Storage | 0.01 | transshipment | Fuel Storage | 1
stacker_reclaimer_1 | Stacker Reclaimer | Stackers | 0.019923 | transshipment | Stackers | 1
stacker_reclaimer_2 | Stacker Reclaimer | Stackers | 0.019923 | transshipment | Stackers | 1
stacker_reclaimer_3 | Stacker Reclaimer | Stackers | 0.019923 | transshipment | Stackers | 1
supply_conv_1 | Supply Conveyor | Supply Conveyors | 0.0033205 | transshipment | Supply Conveyors | 1
supply_conv_2 | Supply Conveyor | Supply Conveyors | 0.0033205 | transshipment | Supply Conveyors | 1
supply_conv_3 | Supply Conveyor | Supply Conveyors | 0.0033205 | transshipment | Supply Conveyors | 1
supply_conv_4 | Supply Conveyor | Supply Conveyors | 0.0033205 | transshipment | Supply Conveyors | 1
feed_conv_1 | Main Feed Conveyor | Feed Conveyors | 0.0066411 | transshipment | Feed Conveyors | 1
feed_conv_2 | Main Feed Conveyor | Feed Conveyors | 0.0066411 | transshipment | Feed Conveyors | 1
water_supply | Fresh Water Supply | Boiler System | 0.02319 | supply | Boiler System | 1
demin_plant | Demineralisation Plant | Boiler System | 0.0086513 | transshipment | Boiler System | 1
boiler_1 | Boiler | Boiler System | 0.14429 | transshipment | Boiler System | 1
boiler_2 | Boiler | Boiler System | 0.14429 | transshipment | Boiler System | 1
precip_1a | Electrostatic Precipitator | Electrostatic Precipitators | 0.0013359 | transshipment | Electrostatic Precipitators | 1
precip_1b | Electrostatic Precipitator | Electrostatic Precipitators | 0.0013359 | transshipment | Electrostatic Precipitators | 1
precip_2a | Electrostatic Precipitator | Electrostatic Precipitators | 0.0013359 | transshipment | Electrostatic Precipitators | 1
precip_2b | Electrostatic Precipitator | Electrostatic Precipitators | 0.0013359 | transshipment | Electrostatic Precipitators | 1
ash_disposal | Ash Disposal System | Emission Management | 0.005 | dependency | Emission Management | 1
stack_1 | Stack | Emission Management | 0.0066793 | transshipment | Emission Management | 1
stack_2 | Stack | Emission Management | 0.0066793 | transshipment | Emission Management | 1
pwr_house | Power House | Generator Plant Subsystem | 0.1 | dependency | none | 1
turbine_condenser_1 | Turbine and Condenser | Condenser | 0.12429 | transshipment | Condenser | 1
turbine_condenser_2 | Turbine and Condenser | Condenser | 0.12429 | transshipment | Condenser | 1
gen_1 | Generator | Generator Plant Subsystem | 0.046543 | transshipment | Generator Plant Subsystem | 1
gen_2 | Generator | Generator Plant Subsystem | 0.046543 | transshipment | Generator Plant Subsystem | 1
tr_1 | Stepup Transformer | Stepup Transformer | 0.012977 | transshipment | Stepup Transformer | 1
tr_2 | Stepup Transformer | Stepup Transformer | 0.012977 | transshipment | Stepup Transformer | 1
output_1 | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | OUTPUT | 1
output_2 | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | OUTPUT | 1

## component_connections
Description: | Network connections. Each pair of nodes is an edge. Directionality is defined by order of nodes in a row (Orig->Dest).
Note: | Used by: (1) network algorithm package for flow calculations, (2) Pygraphviz to draw the system layout.
origin | destination | link_capacity | weight
coal_supply | unloader_1 | 1 | 1
coal_supply | unloader_2 | 1 | 1
unloader_1 | coal_yard | 1 | 1
unloader_2 | coal_yard | 1 | 1
coal_yard | stacker_reclaimer_1 | 1 | 1
coal_yard | stacker_reclaimer_2 | 1 | 1
coal_yard | stacker_reclaimer_3 | 1 | 1
stacker_reclaimer_1 | supply_conv_1 | 1 | 1
stacker_reclaimer_2 | supply_conv_2 | 1 | 1
stacker_reclaimer_3 | supply_conv_3 | 1 | 1
supply_conv_1 | feed_conv_1 | 1 | 1
supply_conv_2 | feed_conv_1 | 1 | 1
supply_conv_3 | feed_conv_2 | 1 | 1
supply_conv_1 | supply_conv_4 | 1 | 1
supply_conv_4 | supply_conv_3 | 1 | 1
supply_conv_3 | supply_conv_4 | 1 | 1
feed_conv_1 | boiler_1 | 1 | 1
feed_conv_2 | boiler_2 | 1 | 1
feed_conv_1 | feed_conv_2 | 1 | 1
demin_plant | boiler_1 | 1 | 1
demin_plant | boiler_2 | 1 | 1
water_supply | demin_plant | 1 | 1
boiler_1 | precip_1a | 1 | 1
boiler_1 | precip_1b | 1 | 1
boiler_2 | precip_2a | 1 | 1
boiler_2 | precip_2b | 1 | 1
precip_1a | stack_1 | 1 | 1
precip_1b | stack_1 | 1 | 1
precip_2a | stack_2 | 1 | 1
precip_2b | stack_2 | 1 | 1
ash_disposal | stack_1 | 1 | 1
ash_disposal | stack_2 | 1 | 1
stack_1 | turbine_condenser_1 | 1 | 1
stack_2 | turbine_condenser_2 | 1 | 1
turbine_condenser_1 | gen_1 | 1 | 1
turbine_condenser_2 | gen_2 | 1 | 1
gen_1 | tr_1 | 1 | 1
gen_2 | tr_2 | 1 | 1
pwr_house | gen_1 | 1 | 1
pwr_house | gen_2 | 1 | 1
tr_1 | output_1 | 1 | 1
tr_2 | output_2 | 1 | 1

## supply_setup
Description: | Capacity at the output nodes on the extremity of the component network
Note: | Capacity given as percentage
input_node | input_capacity | capacity_fraction | commodity_type
coal_supply | 100 | 1 | coal
water_supply | 100 | 1 | water

## output_setup
Description: | Capacity by Generator (in MW)
Note: | Given values are the nominal generation capacities for each generator plant
output_node | production_node | output_node_capacity | capacity_fraction | priority
output_1 | gen_1 | 300 | 0.5 | 2
output_2 | gen_2 | 300 | 0.5 | 1

## comp_type_dmg_algo
Description: | List of component types with fragility and recovery data
Note: | Fragilities are defined according to discrete damage states. Recovery time is in WEEKS. The suffix SDL refers to component Seismic Design Level. [SDL1: 0.2g PGA, SDL2: 0.35g PGA, SDL3: 0.4g PGA]
component_type | damage_state | damage_function | mode | damage_median | damage_logstd | damage_ratio | functionality | minimum | sigma_1 | sigma_2 | recovery_mean | recovery_std | recovery_95percentile | fragility_source
Ash Disposal System | DS1 Slight | Lognormal | 1 | 0.45 | 0.2 | 0.05 | 1 | NA | NA | NA | 0.2 | 0.060796 | 0.1 | SIM to supply conveyor
Ash Disposal System | DS2 Moderate | Lognormal | 1 | 0.59 | 0.3 | 0.3 | 0 | NA | NA | NA | 0.5 | 0.060796 | 0.1 | SIM to supply conveyor
Ash Disposal System | DS3 Extensive | Lognormal | 1 | 0.775 | 0.35 | 0.75 | 0 | NA | NA | NA | 1 | 0.30398 | 0.5 | SIM to supply conveyor
Ash Disposal System | DS4 Complete | Lognormal | 1 | 1 | 0.35 | 1 | 0 | NA | NA | NA | 4.3 | 0.60796 | 1 | SIM to supply conveyor
Boiler | DS1 Slight | Lognormal | 1 | 0.46 | 0.23 | 0.1 | 1 | NA | NA | NA | 3 | 0.60796 | 1
Boiler | DS2 Moderate | Lognormal | 1 | 0.57 | 0.25 | 0.3 | 0 | NA | NA | NA | 20 | 1.2159 | 2
Boiler | DS3 Extensive | Lognormal | 1 | 0.825 | 0.35 | 0.9 | 0 | NA | NA | NA | 60 | 2.4318 | 4
Boiler | DS4 Complete | Lognormal | 1 | 1.8 | 0.6 | 1.3 | 0 | NA | NA | NA | 102.8571 | 4.8637 | 8
Coal Yard | DS1 Slight | Lognormal | 1 | 0.67 | 0.2 | 0.06 | 1 | NA | NA | NA | 0.2 | 0.060796 | 0.1
Coal Yard | DS2 Moderate | Lognormal | 1 | 0.85 | 0.27 | 0.3 | 1 | NA | NA | NA | 0.5 | 0.060796 | 0.1
Coal Yard | DS3 Extensive | Lognormal | 1 | 1.05 | 0.35 | 0.75 | 0 | NA | NA | NA | 1 | 0.30398 | 0.5
Coal Yard | DS4 Complete | Lognormal | 1 | 1.35 | 0.35 | 1 | 0 | NA | NA | NA | 4.3 | 0.60796 | 1
Cooling System | DS1 Slight | Lognormal | 1 | 0.42 | 0.375 | 0.1 | 1 | NA | NA | NA | 1 | 0.30398 | 0.5 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
Cooling System | DS2 Moderate | Lognormal | 1 | 0.57 | 0.375 | 0.3 | 0 | NA | NA | NA | 3 | 0.60796 | 1 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
Cooling System | DS3 Extensive | Lognormal | 1 | 0.78 | 0.475 | 0.75 | 0 | NA | NA | NA | 15 | 1.8239 | 3 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
Cooling System | DS4 Complete | Lognormal | 1 | 1.33 | 0.475 | 1 | 0 | NA | NA | NA | 30 | 2.4318 | 4 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
Demineralisation Plant | DS1 Slight | Lognormal | 1 | 0.42 | 0.16 | 0.1 | 1 | NA | NA | NA | 5 | 0.18239 | 0.3 | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
Demineralisation Plant | DS2 Moderate | Lognormal | 1 | 0.57 | 0.28 | 0.3 | 0 | NA | NA | NA | 10 | 1.2159 | 2 | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
Demineralisation Plant | DS3 Extensive | Lognormal | 1 | 0.78 | 0.35 | 0.75 | 0 | NA | NA | NA | 21 | 1.8239 | 3 | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
Demineralisation Plant | DS4 Complete | Lognormal | 1 | 1.33 | 0.4 | 1 | 0 | NA | NA | NA | 42.8571 | 2.4318 | 4 | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
Electrostatic Precipitator | DS1 Slight | Lognormal | 1 | 0.35 | 0.4 | 0.1 | 0 | NA | NA | NA | 5 | 0.30398 | 0.5 | HAZUS-MH Table D8.8 Electircal equipment
Electrostatic Precipitator | DS2 Moderate | Lognormal | 1 | 0.55 | 0.5 | 0.3 | 0 | NA | NA | NA | 17 | 0.60796 | 1 | HAZUS-MH Table D8.8 Electircal equipment
Electrostatic Precipitator | DS3 Extensive | Lognormal | 1 | 0.75 | 0.4 | 0.75 | 0 | NA | NA | NA | 37 | 1.2159 | 2 | Sim to main feed conveyor
Electrostatic Precipitator | DS4 Complete | Lognormal | 1 | 1 | 0.4 | 1 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4 | Sim to main feed conveyor
Fresh Water Supply | DS1 Slight | Lognormal | 1 | 0.43 | 0.16 | 0.1 | 1 | NA | NA | NA | 1 | 0.12159 | 0.2 | HAZUS-MH MR3 Table 8.6 Small Pumping Plants
Fresh Water Supply | DS2 Moderate | Lognormal | 1 | 0.57 | 0.27 | 0.3 | 0 | NA | NA | NA | 4 | 0.30398 | 0.5
Fresh Water Supply | DS3 Extensive | Lognormal | 1 | 0.78 | 0.35 | 0.75 | 0 | NA | NA | NA | 8 | 0.91194 | 1.5
Fresh Water Supply | DS4 Complete | Lognormal | 1 | 1.33 | 0.4 | 1 | 0 | NA | NA | NA | 12 | 1.8239 | 3
Generator | DS1 Slight | Lognormal | 1 | 0.75 | 0.28 | 0.03 | 0 | NA | NA | NA | 3 | 0.60796 | 1 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
Generator | DS2 Moderate | Lognormal | 1 | 1 | 0.3 | 0.15 | 0 | NA | NA | NA | 20 | 1.2159 | 2 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
Generator | DS3 Extensive | Lognormal | 1 | 1.33 | 0.34 | 0.4 | 0 | NA | NA | NA | 60 | 2.4318 | 4 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
Generator | DS4 Complete | Lognormal | 1 | 1.55 | 0.28 | 1.2 | 0 | NA | NA | NA | 102.8571 | 4.8637 | 8 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
Main Feed Conveyor | DS1 Slight | Lognormal | 1 | 0.45 | 0.2 | 0.06 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5
Main Feed Conveyor | DS2 Moderate | Lognormal | 1 | 0.585 | 0.295 | 0.3 | 0 | NA | NA | NA | 17 | 0.60796 | 1
Main Feed Conveyor | DS3 Extensive | Lognormal | 1 | 0.75 | 0.35 | 0.75 | 0 | NA | NA | NA | 37 | 1.2159 | 2
Main Feed Conveyor | DS4 Complete | Lognormal | 1 | 1 | 0.35 | 1 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4
Power House | DS1 Slight | Lognormal | 1 | 0.475 | 0.25 | 0.06 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5
Power House | DS2 Moderate | Lognormal | 1 | 0.615 | 0.33 | 0.3 | 1 | NA | NA | NA | 17 | 0.60796 | 1
Power House | DS3 Extensive | Lognormal | 1 | 0.77 | 0.4 | 0.75 | 0 | NA | NA | NA | 37 | 1.2159 | 2
Power House | DS4 Complete | Lognormal | 1 | 1 | 0.4 | 1 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4
Stack | DS1 Slight | Lognormal | 1 | 0.67 | 0.2 | 0.1 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5
Stack | DS2 Moderate | Lognormal | 1 | 0.85 | 0.27 | 0.4 | 0 | NA | NA | NA | 17 | 0.60796 | 1
Stack | DS3 Extensive | Lognormal | 1 | 1.05 | 0.35 | 0.8 | 0 | NA | NA | NA | 37 | 1.2159 | 2
Stack | DS4 Complete | Lognormal | 1 | 1.35 | 0.35 | 1.2 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4
Stacker Reclaimer | DS1 Slight | Lognormal | 1 | 0.39 | 0.55 | 0.06 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Stacker Reclaimer | DS2 Moderate | Lognormal | 1 | 0.595 | 0.61 | 0.2 | 0 | NA | NA | NA | 17 | 0.60796 | 1 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Stacker Reclaimer | DS3 Extensive | Lognormal | 1 | 0.795 | 0.595 | 0.8 | 0 | NA | NA | NA | 37 | 1.2159 | 2 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Stacker Reclaimer | DS4 Complete | Lognormal | 1 | 1 | 0.505 | 1.2 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Stepup Transformer | DS1 Slight | Lognormal | 1 | 0.55 | 0.34 | 0.03 | 0 | NA | NA | NA | 5 | 0.30398 | 0.5 | Assume Syner G Table 3.22 230kV with Anchored Sub Components
Stepup Transformer | DS2 Moderate | Lognormal | 1 | 0.9 | 0.26 | 0.1 | 0 | NA | NA | NA | 17 | 0.60796 | 1 | Assume Syner G Table 3.22 230kV with Anchored Sub Components
Stepup Transformer | DS3 Extensive | Lognormal | 1 | 1.25 | 0.21 | 0.15 | 0 | NA | NA | NA | 37 | 1.2159 | 2 | Assume Syner G Table 3.22 230kV with Anchored Sub Components
Stepup Transformer | DS4 Complete | Lognormal | 1 | 1.65 | 0.11 | 1 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4 | Assume Syner G Table 3.22 230kV with Anchored Sub Components
Supply Conveyor | DS1 Slight | Lognormal | 1 | 0.335 | 0.275 | 0.1 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5
Supply Conveyor | DS2 Moderate | Lognormal | 1 | 0.5 | 0.34 | 0.4 | 1 | NA | NA | NA | 17 | 0.60796 | 1
Supply Conveyor | DS3 Extensive | Lognormal | 1 | 0.75 | 0.435 | 0.8 | 0 | NA | NA | NA | 37 | 1.2159 | 2
Supply Conveyor | DS4 Complete | Lognormal | 1 | 1 | 0.455 | 1 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4
Turbine and Condenser | DS1 Slight | Lognormal | 1 | 0.75 | 0.28 | 0.1 | 0 | NA | NA | NA | 5 | 0.60796 | 1
Turbine and Condenser | DS2 Moderate | Lognormal | 1 | 1 | 0.3 | 0.3 | 0 | NA | NA | NA | 20 | 1.2159 | 2
Turbine and Condenser | DS3 Extensive | Lognormal | 1 | 1.33 | 0.34 | 0.85 | 0 | NA | NA | NA | 50 | 2.4318 | 4
Turbine and Condenser | DS4 Complete | Lognormal | 1 | 1.55 | 0.28 | 1.2 | 0 | NA | NA | NA | 102.8571 | 4.8637 | 8
Unloader | DS1 Slight | Lognormal | 1 | 0.44 | 0.55 | 0.06 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Unloader | DS2 Moderate | Lognormal | 1 | 0.645 | 0.61 | 0.2 | 0.6 | NA | NA | NA | 17 | 0.60796 | 1 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Unloader | DS3 Extensive | Lognormal | 1 | 0.845 | 0.595 | 0.8 | 0.2 | NA | NA | NA | 37 | 1.2159 | 2 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Unloader | DS4 Complete | Lognormal | 1 | 1.05 | 0.505 | 1.2 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Ash Disposal System SDL1 | DS1 Slight | Lognormal | 1 | 0.28 | 0.25 | 0.05 | 1 | NA | NA | NA | 0.2 | 0.060796 | 0.1 | Similar to main feed conveyor but with increased variability.
Ash Disposal System SDL1 | DS2 Moderate | Lognormal | 1 | 0.43 | 0.35 | 0.3 | 0 | NA | NA | NA | 0.5 | 0.060796 | 0.1
Ash Disposal System SDL1 | DS3 Extensive | Lognormal | 1 | 0.6 | 0.4 | 0.75 | 0 | NA | NA | NA | 1 | 0.30398 | 0.5
Ash Disposal System SDL1 | DS4 Complete | Lognormal | 1 | 0.85 | 0.4 | 1 | 0 | NA | NA | NA | 4.3 | 0.60796 | 1
Boiler SDL1 | DS1 Slight | Lognormal | 1 | 0.28 | 0.26 | 0.1 | 1 | NA | NA | NA | 3 | 0.60796 | 1 | Using MH Hazus Table D8.8 for Boilers and pressure vessels anchored assuming HAZUS equivalent to 0.3g design level.
Boiler SDL1 | DS2 Moderate | Lognormal | 1 | 0.42 | 0.31 | 0.3 | 0 | NA | NA | NA | 20 | 1.2159 | 2
Boiler SDL1 | DS3 Extensive | Lognormal | 1 | 0.67 | 0.35 | 0.9 | 0 | NA | NA | NA | 60 | 2.4318 | 4
Boiler SDL1 | DS4 Complete | Lognormal | 1 | 1.7 | 0.6 | 1.3 | 0 | NA | NA | NA | 102.8571 | 4.8637 | 8
Coal Yard SDL1 | DS1 Slight | Lognormal | 1 | 0.67 | 0.2 | 0.06 | 1 | NA | NA | NA | 0.2 | 0.060796 | 0.1 | Wind dominance to effective desing resistance of 0.6g
Coal Yard SDL1 | DS2 Moderate | Lognormal | 1 | 0.85 | 0.27 | 0.3 | 1 | NA | NA | NA | 0.5 | 0.060796 | 0.1
Coal Yard SDL1 | DS3 Extensive | Lognormal | 1 | 1.05 | 0.35 | 0.75 | 0 | NA | NA | NA | 1 | 0.30398 | 0.5
Coal Yard SDL1 | DS4 Complete | Lognormal | 1 | 1.35 | 0.35 | 1 | 0 | NA | NA | NA | 4.3 | 0.60796 | 1
Cooling System SDL1 | DS1 Slight | Lognormal | 1 | 0.27 | 0.45 | 0.1 | 1 | NA | NA | NA | 1 | 0.30398 | 0.5 | Assume damage functions for medium water treatment plants MH HAZUS Table 8.3 corresponds with 0.3g design
Cooling System SDL1 | DS2 Moderate | Lognormal | 1 | 0.42 | 0.45 | 0.3 | 0 | NA | NA | NA | 3 | 0.60796 | 1
Cooling System SDL1 | DS3 Extensive | Lognormal | 1 | 0.63 | 0.55 | 0.75 | 0 | NA | NA | NA | 15 | 1.8239 | 3
Cooling System SDL1 | DS4 Complete | Lognormal | 1 | 1.18 | 0.55 | 1 | 0 | NA | NA | NA | 30 | 2.4318 | 4
Demineralisation Plant SDL1 | DS1 Slight | Lognormal | 1 | 0.27 | 0.2 | 0.1 | 1 | NA | NA | NA | 5 | 0.18239 | 0.3 | Using MH Hazus Table 8.3 Small Water Treatment Plant Anchored asuming HAZUS equivalent to 0.3g design level.
Demineralisation Plant SDL1 | DS2 Moderate | Lognormal | 1 | 0.42 | 0.35 | 0.3 | 0 | NA | NA | NA | 10 | 1.2159 | 2
Demineralisation Plant SDL1 | DS3 Extensive | Lognormal | 1 | 0.63 | 0.4 | 0.75 | 0 | NA | NA | NA | 21 | 1.8239 | 3
Demineralisation Plant SDL1 | DS4 Complete | Lognormal | 1 | 1.18 | 0.45 | 1 | 0 | NA | NA | NA | 42.8571 | 2.4318 | 4
Electrostatic Precipitator SDL1 | DS1 Slight | Lognormal | 1 | 0.28 | 0.4 | 0.1 | 0 | NA | NA | NA | 5 | 0.30398 | 0.5 | Assume vulnerability for slight and moderate dominated by high voltage electrical equipment. Use MH HAZUS Table D8.8 for Electrical Equipment Anchored assumed to equate with 0.3g
Electrostatic Precipitator SDL1 | DS2 Moderate | Lognormal | 1 | 0.45 | 0.5 | 0.3 | 0 | NA | NA | NA | 17 | 0.60796 | 1 | Assume vulnerability for slight and moderate dominated by high voltage electrical equipment. Use MH HAZUS Table D8.8 for Electrical Equipment Anchored assumed to equate with 0.3g
Electrostatic Precipitator SDL1 | DS3 Extensive | Lognormal | 1 | 0.6 | 0.4 | 0.75 | 0 | NA | NA | NA | 37 | 1.2159 | 2 | Sim to main feed conveyor
Electrostatic Precipitator SDL1 | DS4 Complete | Lognormal | 1 | 0.85 | 0.4 | 1 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4 | Sim to main feed conveyor
Fresh Water Supply SDL1 | DS1 Slight | Lognormal | 1 | 0.27 | 0.2 | 0.1 | 1 | NA | NA | NA | 1 | 0.12159 | 0.2 | Using MH Hazus Table 8.3 Small Pumping Plant Anchored asuming HAZUS equivalent to 0.3g design level.
Fresh Water Supply SDL1 | DS2 Moderate | Lognormal | 1 | 0.42 | 0.35 | 0.3 | 0 | NA | NA | NA | 4 | 0.30398 | 0.5
Fresh Water Supply SDL1 | DS3 Extensive | Lognormal | 1 | 0.63 | 0.4 | 0.75 | 0 | NA | NA | NA | 8 | 0.91194 | 1.5
Fresh Water Supply SDL1 | DS4 Complete | Lognormal | 1 | 1.18 | 0.45 | 1 | 0 | NA | NA | NA | 12 | 1.8239 | 3
Generator SDL1 | DS1 Slight | Lognormal | 1 | 0.65 | 0.28 | 0.03 | 0 | NA | NA | NA | 3 | 0.60796 | 1
Generator SDL1 | DS2 Moderate | Lognormal | 1 | 0.9 | 0.3 | 0.15 | 0 | NA | NA | NA | 20 | 1.2159 | 2
Generator SDL1 | DS3 Extensive | Lognormal | 1 | 1.23 | 0.34 | 0.4 | 0 | NA | NA | NA | 60 | 2.4318 | 4 | Using MH HAZUS Table D8.8 for Motor Driven Pumps anchored assuming HAZUS equivalent to 0.3g design level - Extensive.
Generator SDL1 | DS4 Complete | Lognormal | 1 | 1.45 | 0.28 | 1.2 | 0 | NA | NA | NA | 102.8571 | 4.8637 | 8
Main Feed Conveyor SDL1 | DS1 Slight | Lognormal | 1 | 0.28 | 0.25 | 0.06 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5
Main Feed Conveyor SDL1 | DS2 Moderate | Lognormal | 1 | 0.43 | 0.35 | 0.3 | 0 | NA | NA | NA | 17 | 0.60796 | 1
Main Feed Conveyor SDL1 | DS3 Extensive | Lognormal | 1 | 0.6 | 0.4 | 0.75 | 0 | NA | NA | NA | 37 | 1.2159 | 2
Main Feed Conveyor SDL1 | DS4 Complete | Lognormal | 1 | 0.85 | 0.4 | 1 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4
Power House SDL1 | DS1 Slight | Lognormal | 1 | 0.28 | 0.25 | 0.06 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5
Power House SDL1 | DS2 Moderate | Lognormal | 1 | 0.43 | 0.35 | 0.3 | 1 | NA | NA | NA | 17 | 0.60796 | 1
Power House SDL1 | DS3 Extensive | Lognormal | 1 | 0.6 | 0.4 | 0.75 | 0 | NA | NA | NA | 37 | 1.2159 | 2
Power House SDL1 | DS4 Complete | Lognormal | 1 | 0.85 | 0.4 | 1 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4
Stack SDL1 | DS1 Slight | Lognormal | 1 | 0.67 | 0.2 | 0.1 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5 | Wind dominance to effective desing resistance of 0.6g
Stack SDL1 | DS2 Moderate | Lognormal | 1 | 0.85 | 0.27 | 0.4 | 0 | NA | NA | NA | 17 | 0.60796 | 1
Stack SDL1 | DS3 Extensive | Lognormal | 1 | 1.05 | 0.35 | 0.8 | 0 | NA | NA | NA | 37 | 1.2159 | 2
Stack SDL1 | DS4 Complete | Lognormal | 1 | 1.35 | 0.35 | 1.2 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4
Stacker Reclaimer SDL1 | DS1 Slight | Lognormal | 1 | 0.3 | 0.5 | 0.06 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5
Stacker Reclaimer SDL1 | DS2 Moderate | Lognormal | 1 | 0.5 | 0.6 | 0.2 | 0 | NA | NA | NA | 17 | 0.60796 | 1 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2 as reference for moderate damage for 0.3g design level.
Stacker Reclaimer SDL1 | DS3 Extensive | Lognormal | 1 | 0.7 | 0.55 | 0.8 | 0 | NA | NA | NA | 37 | 1.2159 | 2
Stacker Reclaimer SDL1 | DS4 Complete | Lognormal | 1 | 0.9 | 0.46 | 1.2 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4
Stepup Transformer SDL1 | DS1 Slight | Lognormal | 1 | 0.4 | 0.45 | 0.03 | 0 | NA | NA | NA | 5 | 0.30398 | 0.5 | Assume Syner G Table 3.22 230kV with Anchored Sub Components represents 0.3g design level.
Stepup Transformer SDL1 | DS2 Moderate | Lognormal | 1 | 0.75 | 0.32 | 0.1 | 0 | NA | NA | NA | 17 | 0.60796 | 1
Stepup Transformer SDL1 | DS3 Extensive | Lognormal | 1 | 1.1 | 0.27 | 0.15 | 0 | NA | NA | NA | 37 | 1.2159 | 2
Stepup Transformer SDL1 | DS4 Complete | Lognormal | 1 | 1.5 | 0.17 | 1 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4
Supply Conveyor SDL1 | DS1 Slight | Lognormal | 1 | 0.24 | 0.3 | 0.1 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5 | Similar to main conveyor but with greater variability.
Supply Conveyor SDL1 | DS2 Moderate | Lognormal | 1 | 0.42 | 0.37 | 0.4 | 1 | NA | NA | NA | 17 | 0.60796 | 1
Supply Conveyor SDL1 | DS3 Extensive | Lognormal | 1 | 0.6 | 0.45 | 0.8 | 0 | NA | NA | NA | 37 | 1.2159 | 2
Supply Conveyor SDL1 | DS4 Complete | Lognormal | 1 | 0.85 | 0.45 | 1 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4
Turbine and Condenser SDL1 | DS1 Slight | Lognormal | 1 | 0.6 | 0.28 | 0.1 | 0 | NA | NA | NA | 5 | 0.60796 | 1 | Using MH Hazus Table D8.8 for Motor Driven Pumps anchored assuming HAZUS equivalent to 0.3g design level - Extensive.
Turbine and Condenser SDL1 | DS2 Moderate | Lognormal | 1 | 0.8 | 0.3 | 0.3 | 0 | NA | NA | NA | 20 | 1.2159 | 2
Turbine and Condenser SDL1 | DS3 Extensive | Lognormal | 1 | 1.18 | 0.34 | 0.85 | 0 | NA | NA | NA | 50 | 2.4318 | 4
Turbine and Condenser SDL1 | DS4 Complete | Lognormal | 1 | 1.4 | 0.28 | 1.2 | 0 | NA | NA | NA | 102.8571 | 4.8637 | 8
Unloader SDL1 | DS1 Slight | Lognormal | 1 | 0.3 | 0.5 | 0.06 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5
Unloader SDL1 | DS2 Moderate | Lognormal | 1 | 0.5 | 0.6 | 0.2 | 0.6 | NA | NA | NA | 17 | 0.60796 | 1 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2 as reference for moderate damage for 0.3g design level.
Unloader SDL1 | DS3 Extensive | Lognormal | 1 | 0.7 | 0.55 | 0.8 | 0.2 | NA | NA | NA | 37 | 1.2159 | 2
Unloader SDL1 | DS4 Complete | Lognormal | 1 | 0.9 | 0.46 | 1.2 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4
Ash Disposal System SDL3 | DS1 Slight | Lognormal | 1 | 0.37 | 0.27 | 0.05 | 1 | NA | NA | NA | 0.2 | 0.060796 | 0.1 | SIM to supply conveyor
Ash Disposal System SDL3 | DS2 Moderate | Lognormal | 1 | 0.55 | 0.32 | 0.3 | 0 | NA | NA | NA | 0.5 | 0.060796 | 0.1 | SIM to supply conveyor
Ash Disposal System SDL3 | DS3 Extensive | Lognormal | 1 | 0.75 | 0.42 | 0.75 | 0 | NA | NA | NA | 1 | 0.30398 | 0.5 | SIM to supply conveyor
Ash Disposal System SDL3 | DS4 Complete | Lognormal | 1 | 1.05 | 0.46 | 1 | 0 | NA | NA | NA | 4.3 | 0.60796 | 1 | SIM to supply conveyor
Boiler SDL3 | DS1 Slight | Lognormal | 1 | 0.4 | 0.55 | 0.1 | 1 | NA | NA | NA | 3 | 0.60796 | 1
Boiler SDL3 | DS2 Moderate | Lognormal | 1 | 0.62 | 0.65 | 0.3 | 0 | NA | NA | NA | 20 | 1.2159 | 2
Boiler SDL3 | DS3 Extensive | Lognormal | 1 | 0.95 | 0.6 | 0.9 | 0 | NA | NA | NA | 60 | 2.4318 | 4
Boiler SDL3 | DS4 Complete | Lognormal | 1 | 1.9 | 0.65 | 1.3 | 0 | NA | NA | NA | 102.8571 | 2.4318 | 4
Coal Yard SDL3 | DS1 Slight | Lognormal | 1 | 0.67 | 0.2 | 0.06 | 1 | NA | NA | NA | 0.2 | 0.060796 | 0.1
Coal Yard SDL3 | DS2 Moderate | Lognormal | 1 | 0.85 | 0.27 | 0.3 | 1 | NA | NA | NA | 0.5 | 0.060796 | 0.1
Coal Yard SDL3 | DS3 Extensive | Lognormal | 1 | 1.05 | 0.35 | 0.75 | 0 | NA | NA | NA | 1 | 0.30398 | 0.5
Coal Yard SDL3 | DS4 Complete | Lognormal | 1 | 1.35 | 0.35 | 1 | 0 | NA | NA | NA | 4.3 | 0.60796 | 1
Cooling System SDL3 | DS1 Slight | Lognormal | 1 | 0.47 | 0.35 | 0.1 | 1 | NA | NA | NA | 1 | 0.30398 | 0.5 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
Cooling System SDL3 | DS2 Moderate | Lognormal | 1 | 0.62 | 0.35 | 0.3 | 0 | NA | NA | NA | 3 | 0.60796 | 1 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
Cooling System SDL3 | DS3 Extensive | Lognormal | 1 | 0.83 | 0.45 | 0.75 | 0 | NA | NA | NA | 15 | 1.8239 | 3 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
Cooling System SDL3 | DS4 Complete | Lognormal | 1 | 1.38 | 0.45 | 1 | 0 | NA | NA | NA | 30 | 2.4318 | 4 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
Demineralisation Plant SDL3 | DS1 Slight | Lognormal | 1 | 0.35 | 0.5 | 0.1 | 1 | NA | NA | NA | 5 | 0.18239 | 0.3 | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
Demineralisation Plant SDL3 | DS2 Moderate | Lognormal | 1 | 0.48 | 0.5 | 0.3 | 0 | NA | NA | NA | 10 | 1.2159 | 2 | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
Demineralisation Plant SDL3 | DS3 Extensive | Lognormal | 1 | 0.63 | 0.6 | 0.75 | 0 | NA | NA | NA | 21 | 1.8239 | 3 | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
Demineralisation Plant SDL3 | DS4 Complete | Lognormal | 1 | 0.93 | 0.6 | 1 | 0 | NA | NA | NA | 42.8571 | 2.4318 | 4 | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
Electrostatic Precipitator SDL3 | DS1 Slight | Lognormal | 1 | 0.35 | 0.5 | 0.1 | 0 | NA | NA | NA | 5 | 0.30398 | 0.5 | HAZUS-MH Table D8.8 Electircal equipment
Electrostatic Precipitator SDL3 | DS2 Moderate | Lognormal | 1 | 0.48 | 0.5 | 0.3 | 0 | NA | NA | NA | 17 | 0.60796 | 1 | HAZUS-MH Table D8.8 Electircal equipment
Electrostatic Precipitator SDL3 | DS3 Extensive | Lognormal | 1 | 0.63 | 0.6 | 0.75 | 0 | NA | NA | NA | 37 | 1.2159 | 2 | Sim to main feed conveyor
Electrostatic Precipitator SDL3 | DS4 Complete | Lognormal | 1 | 0.93 | 0.6 | 1 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4 | Sim to main feed conveyor
Fresh Water Supply SDL3 | DS1 Slight | Lognormal | 1 | 0.25 | 0.7 | 0.1 | 1 | NA | NA | NA | 1 | 0.12159 | 0.2 | HAZUS-MH MR3 Table 8.6 Small Pumping Plants
Fresh Water Supply SDL3 | DS2 Moderate | Lognormal | 1 | 0.46 | 0.65 | 0.3 | 0 | NA | NA | NA | 4 | 0.30398 | 0.5
Fresh Water Supply SDL3 | DS3 Extensive | Lognormal | 1 | 0.76 | 0.65 | 0.75 | 0 | NA | NA | NA | 8 | 0.91194 | 1.5
Fresh Water Supply SDL3 | DS4 Complete | Lognormal | 1 | 1.6 | 0.8 | 1 | 0 | NA | NA | NA | 12 | 1.8239 | 3
Generator SDL3 | DS1 Slight | Lognormal | 1 | 0.8 | 0.28 | 0.03 | 0 | NA | NA | NA | 3 | 0.60796 | 1 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
Generator SDL3 | DS2 Moderate | Lognormal | 1 | 1.05 | 0.3 | 0.15 | 0 | NA | NA | NA | 20 | 1.2159 | 2 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
Generator SDL3 | DS3 Extensive | Lognormal | 1 | 1.38 | 0.34 | 0.4 | 0 | NA | NA | NA | 60 | 2.4318 | 4 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
Generator SDL3 | DS4 Complete | Lognormal | 1 | 1.6 | 0.28 | 1.2 | 0 | NA | NA | NA | 102.8571 | 4.8637 | 8 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
Main Feed Conveyor SDL3 | DS1 Slight | Lognormal | 1 | 0.37 | 0.21 | 0.06 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5
Main Feed Conveyor SDL3 | DS2 Moderate | Lognormal | 1 | 0.55 | 0.26 | 0.3 | 0 | NA | NA | NA | 17 | 0.60796 | 1
Main Feed Conveyor SDL3 | DS3 Extensive | Lognormal | 1 | 0.75 | 0.36 | 0.75 | 0 | NA | NA | NA | 37 | 1.2159 | 2
Main Feed Conveyor SDL3 | DS4 Complete | Lognormal | 1 | 1.05 | 0.4 | 1 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4
Power House SDL3 | DS1 Slight | Lognormal | 1 | 0.27 | 0.25 | 0.06 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5
Power House SDL3 | DS2 Moderate | Lognormal | 1 | 0.45 | 0.32 | 0.3 | 1 | NA | NA | NA | 17 | 0.60796 | 1
Power House SDL3 | DS3 Extensive | Lognormal | 1 | 0.65 | 0.4 | 0.75 | 0 | NA | NA | NA | 37 | 1.2159 | 2
Power House SDL3 | DS4 Complete | Lognormal | 1 | 0.95 | 0.4 | 1 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4
Stack SDL3 | DS1 Slight | Lognormal | 1 | 0.67 | 0.2 | 0.1 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5
Stack SDL3 | DS2 Moderate | Lognormal | 1 | 0.85 | 0.27 | 0.4 | 0 | NA | NA | NA | 17 | 0.60796 | 1
Stack SDL3 | DS3 Extensive | Lognormal | 1 | 1.05 | 0.35 | 0.8 | 0 | NA | NA | NA | 37 | 1.2159 | 2
Stack SDL3 | DS4 Complete | Lognormal | 1 | 1.35 | 0.35 | 1.2 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4
Stacker Reclaimer SDL3 | DS1 Slight | Lognormal | 1 | 0.4 | 0.5 | 0.06 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Stacker Reclaimer SDL3 | DS2 Moderate | Lognormal | 1 | 0.6 | 0.6 | 0.2 | 0 | NA | NA | NA | 17 | 0.60796 | 1 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Stacker Reclaimer SDL3 | DS3 Extensive | Lognormal | 1 | 0.8 | 0.55 | 0.8 | 0 | NA | NA | NA | 37 | 1.2159 | 2 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Stacker Reclaimer SDL3 | DS4 Complete | Lognormal | 1 | 1 | 0.46 | 1.2 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Stepup Transformer SDL3 | DS1 Slight | Lognormal | 1 | 0.6 | 0.32 | 0.03 | 0 | NA | NA | NA | 5 | 0.30398 | 0.5 | Assume Syner G Table 3.22 230kV with Anchored Sub Components
Stepup Transformer SDL3 | DS2 Moderate | Lognormal | 1 | 0.95 | 0.24 | 0.1 | 0 | NA | NA | NA | 17 | 0.60796 | 1 | Assume Syner G Table 3.22 230kV with Anchored Sub Components
Stepup Transformer SDL3 | DS3 Extensive | Lognormal | 1 | 1.3 | 0.19 | 0.15 | 0 | NA | NA | NA | 37 | 1.2159 | 2 | Assume Syner G Table 3.22 230kV with Anchored Sub Components
Stepup Transformer SDL3 | DS4 Complete | Lognormal | 1 | 1.7 | 0.09 | 1 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4 | Assume Syner G Table 3.22 230kV with Anchored Sub Components
Supply Conveyor SDL3 | DS1 Slight | Lognormal | 1 | 0.37 | 0.27 | 0.1 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5
Supply Conveyor SDL3 | DS2 Moderate | Lognormal | 1 | 0.55 | 0.32 | 0.4 | 1 | NA | NA | NA | 17 | 0.60796 | 1
Supply Conveyor SDL3 | DS3 Extensive | Lognormal | 1 | 0.85 | 0.42 | 0.8 | 0 | NA | NA | NA | 37 | 1.2159 | 2
Supply Conveyor SDL3 | DS4 Complete | Lognormal | 1 | 1.05 | 0.46 | 1 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4
Turbine and Condenser SDL3 | DS1 Slight | Lognormal | 1 | 0.8 | 0.28 | 0.1 | 0 | NA | NA | NA | 5 | 0.60796 | 1
Turbine and Condenser SDL3 | DS2 Moderate | Lognormal | 1 | 1.05 | 0.3 | 0.3 | 0 | NA | NA | NA | 20 | 1.2159 | 2
Turbine and Condenser SDL3 | DS3 Extensive | Lognormal | 1 | 1.38 | 0.34 | 0.85 | 0 | NA | NA | NA | 50 | 2.4318 | 4
Turbine and Condenser SDL3 | DS4 Complete | Lognormal | 1 | 1.6 | 0.28 | 1.2 | 0 | NA | NA | NA | 102.8571 | 4.8637 | 8
Unloader SDL3 | DS1 Slight | Lognormal | 1 | 0.5 | 0.5 | 0.06 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Unloader SDL3 | DS2 Moderate | Lognormal | 1 | 0.7 | 0.6 | 0.2 | 0.6 | NA | NA | NA | 17 | 0.60796 | 1 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Unloader SDL3 | DS3 Extensive | Lognormal | 1 | 0.9 | 0.55 | 0.8 | 0.2 | NA | NA | NA | 37 | 1.2159 | 2 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Unloader SDL3 | DS4 Complete | Lognormal | 1 | 1.1 | 0.46 | 1.2 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4 | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Switch Yard | DS1 Slight | Lognormal | 1 | 0.11 | 0.7 | 0.3 | 1 | NA | NA | NA | 1 | 0.30398 | 0.5 | HAZUS-MH MR3 Table 8.22.a Substations
Switch Yard | DS2 Moderate | Lognormal | 1 | 0.15 | 0.75 | 0.6 | 0.6 | NA | NA | NA | 3 | 0.91194 | 1.5 | HAZUS-MH MR3 Table 8.22.a Substations
Switch Yard | DS3 Extensive | Lognormal | 1 | 0.2 | 0.75 | 0.8 | 0.2 | NA | NA | NA | 7 | 2.1278 | 3.5 | HAZUS-MH MR3 Table 8.22.a Substations
Switch Yard | DS4 Complete | Lognormal | 1 | 0.47 | 0.7 | 1 | 0 | NA | NA | NA | 30 | 9.1194 | 15 | HAZUS-MH MR3 Table 8.22.a Substations
SYSTEM_OUTPUT | DS1 Slight | Lognormal | 1 | 10 | 0.01 | 0.01 | 1 | NA | NA | NA | 1 | 0.060796 | 0.1
SYSTEM_OUTPUT | DS2 Moderate | Lognormal | 1 | 10 | 0.01 | 0.01 | 1 | NA | NA | NA | 1 | 0.060796 | 0.1
SYSTEM_OUTPUT | DS3 Extensive | Lognormal | 1 | 10 | 0.01 | 0.01 | 1 | NA | NA | NA | 1 | 0.060796 | 0.1
SYSTEM_OUTPUT | DS4 Complete | Lognormal | 1 | 10 | 0.01 | 0.01 | 1 | NA | NA | NA | 1 | 0.060796 | 0.1
SYSTEM_INPUT | DS1 Slight | Lognormal | 1 | 10 | 0.01 | 0.01 | 1 | NA | NA | NA | 1 | 0.060796 | 0.1
SYSTEM_INPUT | DS2 Moderate | Lognormal | 1 | 10 | 0.01 | 0.01 | 1 | NA | NA | NA | 1 | 0.060796 | 0.1
SYSTEM_INPUT | DS3 Extensive | Lognormal | 1 | 10 | 0.01 | 0.01 | 1 | NA | NA | NA | 1 | 0.060796 | 0.1
SYSTEM_INPUT | DS4 Complete | Lognormal | 1 | 10 | 0.01 | 0.01 | 1 | NA | NA | NA | 1 | 0.060796 | 0.1

## damage_state_def
Description: | Definitions of damage states of the list of component types in the system
Note:
component_type | damage_state | damage_state_definition
Ash Disposal System | DS1 Slight | Minor deformation to supporting structure with some yielding of hold-down bolts.
Ash Disposal System | DS2 Moderate | Significant deformaton to steel supporting structure with misaligment of ash handling conveyors
Ash Disposal System | DS3 Extensive | Horizontal displacement of structure with failure of bracing elements and damage to ash silo structure.
Ash Disposal System | DS4 Complete | Partial or complete collapse of ash handling system.
Boiler | DS1 Slight | Minor deformation to supporting structure and minor damage at lateral restraint points to boiler. No internal damage to boiler.
Boiler | DS2 Moderate | Significant deformation to supporting structure with deformation at holding down bolts and yielding of bracing elements. Damage to internal boiler pipes requiring access for repair.
Boiler | DS3 Extensive | Major damage to boiler support with failure of many bracing elements. Large deformations damage connecting pipework. Widespread damage to internal steam pipes in boiler requring extensive replacement.
Boiler | DS4 Complete | Damage beyond repair
Coal Yard | DS1 Slight | Minor deformations in connections or hairline cracks in a few welds. Minor brace deformation. Some deformation at hold down bolts.
Coal Yard | DS2 Moderate | Some steel members have yielded exhibiting observable permanent rotations at connections. A few welded connections may exhibit major cracks through welds or a few bolted connections may exhibit broken bolts or enlarged bolt holes. Some yielding of braces and soem anchor bolts stretched.
Coal Yard | DS3 Extensive | Many steel bracing elements have exceeded their yield capacity resulting in significant permanent lateral deformation of the structure. Many truss arch members have buckeld in compression. Some of the structural connections may have exceeded their ultimate capacity exhibited by major permanent member rotations at connections, buckled flanges and failed connections. Some foundation oviement due to settlement and some anchor bolts failed.
Coal Yard | DS4 Complete | A significant proportion of the structural elements have exceeded their ultimate capacities or some critical structural elements or connections have failed resulting in dangerous permanent lateral displacement, partial collapse or collapse of the shelter structure.
Cooling System | DS1 Slight | Minor damage to water handling pumps and pipework. Minor damage to pumphouse superstructure.
Cooling System | DS2 Moderate | Moderate structural damage to pumphouse superstructure. Deformation of pump hold-down and pipework with some leakage at flanges and valves. Some movement of pumphouse substructure due to liquefaction.
Cooling System | DS3 Extensive | Rupture of some water mains due to failure of supporting strucuture. Significant movement of pumps and motors leading to some misalignment. Extensive damage to pumphouse superstructure, power supply and control panels. Movement of pumphouse substructure and other valve chambers leading to damage to water mains.
Cooling System | DS4 Complete | Damage beyond repair.
Demineralisation Plant | DS1 Slight | Minor damage to water handling pumps and pipework. Minor damage to plant superstructure.
Demineralisation Plant | DS2 Moderate | Moderate structural damage to demin plant superstructure. Deformation of pump hold-down and pipework with some leakage at flanges and valves. Some movement of pumphouse substructure due to liquefaction.
Demineralisation Plant | DS3 Extensive | Rupture of some water mains due to failure of supporting strucuture. Significant movement of pumps and motors leading to some misalignment. Extensive damage to demin plant superstructure, power supply and control panels. Movement of demin substructure and other valve chambers significant leading to damage to water mains.
Demineralisation Plant | DS4 Complete | Damage beyond repair.
Electrostatic Precipitator | DS1 Slight | minor damage to supporting structure and electrical equipment
Electrostatic Precipitator | DS2 Moderate | significant deformation to supporting structure. Leakage of flue gases. Some damage to internal discharge electrodes and collector panels.
Electrostatic Precipitator | DS3 Extensive | Major deformation of supporting structure with failure of key bracing elements and permanent offset. Internal discharge electrodes and collector panels extensively damaged. Damage to high voltage power supply and control equipment.
Electrostatic Precipitator | DS4 Complete | Damage beyond repair.
Fresh Water Supply | DS1 Slight | Minor movement of intake structure and minor damage to freshwater pumps and pipework.
Fresh Water Supply | DS2 Moderate | Partial liquefaction of soils in the vicinity of intake structure leading to some horizontal movement and rotation with attendent damage to pipework. Horizontal movement to freshwater pumps and peripheral pipework.
Fresh Water Supply | DS3 Extensive | Extensive liquefaction leading to large scale movement of intake structures with major damage to both pipework and pumping facilities. Control equipment damaged.
Fresh Water Supply | DS4 Complete | Damage beyond repair
Generator | DS1 Slight | Minor damage to generator electrical connectivity. Some horizonrtal deformation to generator support with distortion of holding down bolts.
Generator | DS2 Moderate | Significant horizontal deformation leading to misalignment of generator to turbine shaft.
Generator | DS3 Extensive | Large horizontal deformation of both condensor and turbine relative to supporting plinth leading to damage to generator to turbine shaft requiring replacement.
Generator | DS4 Complete | Irreparable damage to generator.
Main Feed Conveyor | DS1 Slight | Minor deformation of support structure with some yeilding of holding down bolts.
Main Feed Conveyor | DS2 Moderate | Significant deformation of supporting structure with horizontal displacement of conveyor system. Misalignment of feed conveyors.
Main Feed Conveyor | DS3 Extensive | Major damage to supporting structure with failure of bracing elelments. Damage to seating of conveyor structure on supporting frame. Possible permanent drift due to foundation settlement.
Main Feed Conveyor | DS4 Complete | Partial or complete collapse.
Power House | DS1 Slight | Minor deformations in connections or hairline cracks in a few welds. Minor brace deformation. Minor spalling at some precast panel corners.
Power House | DS2 Moderate | Some steel members have yielded exhibiting observable permanent rotations at connections. A few welded connections may exhibit major cracks through welds or a few bolted connections may exhibit broken bolts or enlarged bolt holes. Some yielding of braces. More significant spalling damage to precast panels with deformation at panel connections.
Power House | DS3 Extensive | Most steel members have exceeded their yield capacity resulting in significant permanent lateral deformation of the structure. Some of the structural members or connections may have exceeded their ultimate capacity exhibited by major permanent member rotations at connections, buckled flanges and failed connections. Some anchor bolts stretched. Partial collapse of portions of the structure may have occurred due to failed critical elements or connections.
Power House | DS4 Complete | A significant proportion of the structural elements have exceeded their ultimate capacities or some critical structural elements or connections have failed resulting in dangerous permanent lateral displacement, partial collapse or collapse of the building.
Stack | DS1 Slight | Minor damage to structure with deformation of holding down bolts and with some bracing connections.
Stack | DS2 Moderate | Significant deformation of supporting structure with horizontal displacement. Yielding of bracing elements. Damage to flue leading to gas leakage.
Stack | DS3 Extensive | Major horizontal deformation with permanent drift. Failure of bracing elements and extensive damage to flue with many leakage points.
Stack | DS4 Complete | Damage beyond repair including collapse.
Stacker Reclaimer | DS1 Slight | Minor deformation to rail support and stacker reclaimer bracing elements.
Stacker Reclaimer | DS2 Moderate | Significant deformation of stacker structural elements leading to misalignment of machine components and conveyors.
Stacker Reclaimer | DS3 Extensive | Ground deformation leading to gross movement of support rails. Failure of bracing elements on stacker leading to permanent distortion of equipment. Damage to power supply and control equipment.
Stacker Reclaimer | DS4 Complete | Overturning with major distortion of structural elements.
Stepup Transformer | DS1 Slight | Porcelain Gasket Leak
Stepup Transformer | DS2 Moderate | Porcelain Break, Major break in Radiator
Stepup Transformer | DS3 Extensive | Anchorage Failure
Stepup Transformer | DS4 Complete | Overturn
Supply Conveyor | DS1 Slight | Minor deformation of support structure with some yeilding of holding down bolts.
Supply Conveyor | DS2 Moderate | Significant deformation of supporting structure with horizontal displacement of conveyor system. Misalignment of feed conveyors.
Supply Conveyor | DS3 Extensive | Major damage to supporting structure with failure of bracing elelments. Damage to seating of conveyor structure on supporting frame. Possible permanent drift due to foundation settlement.
Supply Conveyor | DS4 Complete | Partial or complete collapse.
Turbine and Condenser | DS1 Slight | Minor damage to condensor pipework. Some horizontal deformation of condensor support connections and steam supply to turbine.
Turbine and Condenser | DS2 Moderate | Significant horizontal deformation of both condensor and turbine relative to supporting plinth leading to misalignment of turbine shaft to generator and steam leakage in pipework.
Turbine and Condenser | DS3 Extensive | Large horizontal deformation of both condensor and turbine relative to supporting plinth leading to damage to turbine shaft to generator requiring replacement. Internal damage to condensor requiring replacement.
Turbine and Condenser | DS4 Complete | Irreparable damage to turbine and condensor.
Unloader | DS1 Slight | Minor deformation to rail support and unloader bracing frame elements.
Unloader | DS2 Moderate | Significant deformation of unloader structural elements leading to misalignment of machine components and conveyors. Minor derailment from tracks on wharf.
Unloader | DS3 Extensive | Failure of bracing elements on unloader leading to permanent distortion of equipment. Damage to power supply and control equipment. Major derailment.
Unloader | DS4 Complete | Overturning with major distortion of structural elements.
Switch Yard | DS1 Slight
Switch Yard | DS2 Moderate
Switch Yard | DS3 Extensive
Switch Yard | DS4 Complete
SYSTEM_OUTPUT | DS1 Slight
SYSTEM_OUTPUT | DS2 Moderate
SYSTEM_OUTPUT | DS3 Extensive
SYSTEM_OUTPUT | DS4 Complete
SYSTEM_INPUT | DS1 Slight
SYSTEM_INPUT | DS2 Moderate
SYSTEM_INPUT | DS3 Extensive
SYSTEM_INPUT | DS4 Complete

## comp_type_dmg_algo 0.2g
Description: | List of component types with fragility and recovery data
Note: | Fragilities are defined according to discrete damage states. Recovery time is in WEEKS.
component_type | damage_state | damage_med | damage_logstd | damage_ratio | functionality | recovery_mean | recovery_std |  | Source
Ash Disposal System SDL1 | DS1 Slight | 0.28 | 0.25 | 0.05 | 1 | 0.2 | 0.5 | Minor deformation to supporting structure with some yielding of hold-down bolts. | Similar to main feed conveyor but with increased variability.
Ash Disposal System SDL1 | DS2 Moderate | 0.43 | 0.35 | 0.3 | 0 | 0.5 | 1.5 | Significant deformaton to steel supporting structure with misaligment of ash handling conveyors
Ash Disposal System SDL1 | DS3 Extensive | 0.6 | 0.4 | 0.75 | 0 | 1 | 3.5 | Horizontal displacement of structure with failure of bracing elements and damage to ash silo structure.
Ash Disposal System SDL1 | DS4 Complete | 0.85 | 0.4 | 1 | 0 | 4.2857 | 15 | Partial or complete collapse of ash handling system.
Boiler SDL1 | DS1 Slight | 0.28 | 0.26 | 0.1 | 1 | 3 | 1 | Minor deformation to supporting structure and minor damage at lateral restraint points to boiler. No internal damage to boiler. | Using MH Hazus Table D8.8 for Boilers and pressue Vessels Anchored assuming HAZUS equivalent to 0.3g design level. Adjustments made to beat to reflect Mindoro Eqke outcomes.
Boiler SDL1 | DS2 Moderate | 0.42 | 0.31 | 0.3 | 0 | 20 | 4 | Significant deformation to supporting structure with deformation at holding down bolts and yielding of bracing elements. Damage to internal boiler pipes requiring access for repair.
Boiler SDL1 | DS3 Extensive | 0.67 | 0.35 | 0.9 | 0 | 60 | 10 | Major damage to boiler support with failure of many bracing elements. Large deformations damage connecting pipework. Widespread damage to internal steam pipes in boiler requring extensive replacement.
Boiler SDL1 | DS4 Complete | 1.7 | 0.6 | 1.3 | 0 | 102.8571 | 20 | Damage beyond repair
Turbine and Condenser SDL1 | DS1 Slight | 0.6 | 0.28 | 0.1 | 1 | 5 | 0.5 | Minor damage to condensor pipework. Some horizontal deformation of condensor support connections and steam supply to turbine. | Using MH Hazus Table D8.8 for Motor Driven Pumps anchored assuming HAZUS equivalent to 0.3g design level - Extensive.
Turbine and Condenser SDL1 | DS2 Moderate | 0.8 | 0.3 | 0.3 | 0 | 20 | 1.5 | Significant horizontal deformation of both condensor and turbine relative to supporting plinth leading to misalignment of turbine shaft to generator and steam leakage in pipework.
Turbine and Condenser SDL1 | DS3 Extensive | 1.18 | 0.34 | 0.85 | 0 | 50 | 3.5 | Large horizontal deformation of both condensor and turbine relative to supporting plinth leading to damage to turbine shaft to generator requiring replacement. Internal damage to condensor requiring replacement.
Turbine and Condenser SDL1 | DS4 Complete | 1.4 | 0.28 | 1.2 | 0 | 102.8571 | 15 | Irreparable damage to turbine and condensor.
Cooling System SDL1 | DS1 Slight | 0.27 | 0.45 | 0.1 | 1 | 1 | 0.5 | Minor damage to water handling pumps and pipework. Minor damage to pumphouse superstructure. | Assume damage functions for medium water treatment plants MH HAZUS Table 8.3 corresponds with 0.3g design
Cooling System SDL1 | DS2 Moderate | 0.42 | 0.45 | 0.3 | 0 | 3 | 1.5 | Moderate structural damage to pumphouse superstructure. Deformation of pump hold-down and pipework with some leakage at flanges and valves. Some movement of pumphouse substructure due to liquefaction.
Cooling System SDL1 | DS3 Extensive | 0.63 | 0.55 | 0.75 | 0 | 7 | 3.5 | Rupture of some water mains due to failure of supporting strucuture. Significant movement of pumps and motors leading to some misalignment. Extensive damage to pumphouse superstructure, power supply and control panels. Movement of pumphouse substructure and other valve chambers leading to damage to water mains.
Cooling System SDL1 | DS4 Complete | 1.18 | 0.55 | 1 | 0 | 30 | 15 | Damage beyond repair.
Demineralisation Plant SDL1 | DS1 Slight | 0.27 | 0.2 | 0.1 | 1 | 5 | 0.3 | Minor damage to water handling pumps and pipework. Minor damage to plant superstructure. | Using MH Hazus Table 8.4 Medium Water Treatment Plant Anchored assuming HAZUS equivalent to 0.3g design level. Adjustment made to beta to reflect Mindoro eqke outcomes.
Demineralisation Plant SDL1 | DS2 Moderate | 0.42 | 0.35 | 0.3 | 0 | 10 | 2.7 | Moderate structural damage to demin plant superstructure. Deformation of pump hold-down and pipework with some leakage at flanges and valves. Some movement of pumphouse substructure due to liquefaction.
Demineralisation Plant SDL1 | DS3 Extensive | 0.63 | 0.4 | 0.75 | 0 | 21 | 10 | Rupture of some water mains due to failure of supporting strucuture. Significant movement of pumps and motors leading to some misalignment. Extensive damage to demin plant superstructure, power supply and control panels. Movement of demin substructure and other valve chambers significant leading to damage to water mains.
Demineralisation Plant SDL1 | DS4 Complete | 1.18 | 0.45 | 1 | 0 | 42.8571 | 18 | Damage beyond repair.
Electrostatic Precipitator SDL1 | DS1 Slight | 0.28 | 0.4 | 0.1 | 1 | 5 | 0.5 | minor damage to supporting structure and electrical equipment | Assume vulnerability for slight and moderate dominated by high voltage electrical equipment. Use MH HAZUS Table D8.8 for Electrical Equipment Anchored assumed to equate with 0.3g
Electrostatic Precipitator SDL1 | DS2 Moderate | 0.45 | 0.5 | 0.3 | 0 | 17 | 0.5 | significant deformation to supporting structure. Leakage of flue gases. Some damage to internal discharge electrodes and collector panels. | Assume vulnerability for slight and moderate dominated by high voltage electrical equipment. Use MH HAZUS Table D8.8 for Electrical Equipment Anchored assumed to equate with 0.3g
Electrostatic Precipitator SDL1 | DS3 Extensive | 0.6 | 0.4 | 0.75 | 0 | 37 | 1.5 | Major deformation of supporting structure with failure of key bracing elements and permanent offset. Internal discharge electrodes and collector panels extensively damaged. Damage to high voltage power supply and control equipment. | Sim to main feed conveyor
Electrostatic Precipitator SDL1 | DS4 Complete | 0.85 | 0.4 | 1 | 0 | 77.1429 | 3 | Damage beyond repair. | Sim to main feed conveyor
Main Feed Conveyor SDL1 | DS1 Slight | 0.28 | 0.25 | 0.06 | 1 | 5 | 0.5 | Minor deformation of support structure with some yeilding of holding down bolts.
Main Feed Conveyor SDL1 | DS2 Moderate | 0.43 | 0.35 | 0.3 | 0 | 17 | 1.5 | Significant deformation of supporting structure with horizontal displacement of conveyor system. Misalignment of feed conveyors.
Main Feed Conveyor SDL1 | DS3 Extensive | 0.6 | 0.4 | 0.75 | 0 | 37 | 3.5 | Major damage to supporting structure with failure of bracing elelments. Damage to seating of conveyor structure on supporting frame. Possible permanent drift due to foundation settlement.
Main Feed Conveyor SDL1 | DS4 Complete | 0.85 | 0.4 | 1 | 0 | 77.1429 | 15 | Partial or complete collapse.
Fresh Water Source SDL1 | DS1 Slight | 0.27 | 0.2 | 0.1 | 1 | 1 | 0.2 | Minor movement of intake structure and minor damage to freshwater pumps and pipework. | Using MH Hazus Table 8.4 Medium Water Treatment Plant Anchored assuming HAZUS equivalent to 0.3g design level. Adjustment made to beta to reflect Mindoro eqke outcomes.
Fresh Water Source SDL1 | DS2 Moderate | 0.42 | 0.35 | 0.3 | 0 | 4 | 0.5 | Partial liquefaction of soils in the vicinity of intake structure leading to some horizontal movement and rotation with attendent damage to pipework. Horizontal movement to freshwater pumps and peripheral pipework.
Fresh Water Source SDL1 | DS3 Extensive | 0.63 | 0.4 | 0.75 | 0 | 8 | 1.5 | Extensive liquefaction leading to large scale movement of intake structures with major damage to both pipework and pumping facilities. Control equipment damaged.
Fresh Water Source SDL1 | DS4 Complete | 1.18 | 0.45 | 1 | 0 | 12 | 3 | Damage beyond repair
Power House SDL1 | DS1 Slight | 0.28 | 0.25 | 0.06 | 1 | 1 | 0.2 | Minor deformations in connections or hairline cracks in a few welds. Minor brace deformation. Minor spalling at some precast panel corners.
Power House SDL1 | DS2 Moderate | 0.43 | 0.35 | 0.3 | 1 | 4 | 0.5 | Some steel members have yielded exhibiting observable permanent rotations at connections. A few welded connections may exhibit major cracks through welds or a few bolted connections may exhibit broken bolts or enlarged bolt holes. Some yielding of braces. More significant spalling damage to precast panels with deformation at panel connections.
Power House SDL1 | DS3 Extensive | 0.6 | 0.4 | 0.75 | 0 | 8 | 1.5 | Most steel members have exceeded their yield capacity resulting in significant permanent lateral deformation of the structure. Some of the structural members or connections may have exceeded their ultimate capacity exhibited by major permanent member rotations at connections, buckled flanges and failed connections. Some anchor bolts stretched. Partial collapse of portions of the structure may have occurred due to failed critical elements or connections.
Power House SDL1 | DS4 Complete | 0.85 | 0.4 | 1 | 0 | 12 | 3 | A significant proportion of the structural elements have exceeded their ultimate capacities or some critical structural elements or connections have failed resulting in dangerous permanent lateral displacement, partial collapse or collapse of the building.
Stack SDL1 | DS1 Slight | 0.67 | 0.2 | 0.1 | 1 | 5 | 0.5 | Minor damage to structure with deformation of holding down bolts and with some bracing connections. | Wind dominance to effective desing resistance of 0.6g
Stack SDL1 | DS2 Moderate | 0.85 | 0.27 | 0.4 | 0 | 17 | 1.5 | Significant deformation of supporting structure with horizontal displacement. Yielding of bracing elements. Damage to flue leading to gas leakage.
Stack SDL1 | DS3 Extensive | 1.05 | 0.35 | 0.8 | 0 | 37 | 3.5 | Major horizontal deformation with permanent drift. Failure of bracing elements and extensive damage to flue with many leakage points.
Stack SDL1 | DS4 Complete | 1.35 | 0.35 | 1.2 | 0 | 77.1429 | 15 | Damage beyond repair including collapse.
Stacker Reclaimer SDL1 | DS1 Slight | 0.3 | 0.5 | 0.06 | 1 | 5 | 0.5 | Minor deformation to rail support and stacker reclaimer bracing elements.
Stacker Reclaimer SDL1 | DS2 Moderate | 0.5 | 0.6 | 0.2 | 0 | 17 | 1.5 | Significant deformation of stacker structural elements leading to misalignment of machine components and conveyors. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2 as reference for moderate damage for 0.3g design level.
Stacker Reclaimer SDL1 | DS3 Extensive | 0.7 | 0.55 | 0.8 | 0 | 37 | 3.5 | Ground deformation leading to gross movement of support rails. Failure of bracing elements on stacker leading to permanent distortion of equipment. Damage to power supply and control equipment.
Stacker Reclaimer SDL1 | DS4 Complete | 0.9 | 0.46 | 1.2 | 0 | 77.1429 | 15 | Overturning with major distortion of structural elements.
Stepup Transformer SDL1 | DS1 Slight | 0.4 | 0.45 | 0.03 | 1 | 5 | 0.5 | Porcelain Gasket Leak | Assume Syner G Table 3.22 230kV with Anchored Sub Components represents 0.3g design level.
Stepup Transformer SDL1 | DS2 Moderate | 0.75 | 0.32 | 0.1 | 0 | 17 | 1.5 | Porcelain Break, Major break in Radiator
Stepup Transformer SDL1 | DS3 Extensive | 1.1 | 0.27 | 0.15 | 0 | 37 | 3.5 | Anchorage Failure
Stepup Transformer SDL1 | DS4 Complete | 1.5 | 0.17 | 1 | 0 | 77.1429 | 15 | Overturn
Supply Conveyor SDL1 | DS1 Slight | 0.24 | 0.3 | 0.1 | 1 | 5 | 0.5 | Minor deformation of support structure with some yeilding of holding down bolts. | Similar to main conveyor but with greater variability.
Supply Conveyor SDL1 | DS2 Moderate | 0.42 | 0.37 | 0.4 | 1 | 17 | 1.5 | Significant deformation of supporting structure with horizontal displacement of conveyor system. Misalignment of feed conveyors.
Supply Conveyor SDL1 | DS3 Extensive | 0.6 | 0.45 | 0.8 | 0 | 37 | 3.5 | Major damage to supporting structure with failure of bracing elelments. Damage to seating of conveyor structure on supporting frame. Possible permanent drift due to foundation settlement.
Supply Conveyor SDL1 | DS4 Complete | 0.85 | 0.45 | 1 | 0 | 77.1429 | 15 | Partial or complete collapse.
Generator SDL1 | DS1 Slight | 0.65 | 0.28 | 0.03 | 1 | 3 | 1 | Minor damage to generator electrical connectivity. Some horizonrtal deformation to generator support with distortion of holding down bolts.
Generator SDL1 | DS2 Moderate | 0.9 | 0.3 | 0.15 | 0 | 20 | 4 | Significant horizontal deformation leading to misalignment of generator to turbine shaft.
Generator SDL1 | DS3 Extensive | 1.23 | 0.34 | 0.4 | 0 | 60 | 10 | Large horizontal deformation of both condensor and turbine relative to supporting plinth leading to damage to generator to turbine shaft requiring replacement. | Using MH HAZUS Table D8.8 for Motor Driven Pumps anchored assuming HAZUS equivalent to 0.3g design level - Extensive.
Generator SDL1 | DS4 Complete | 1.45 | 0.28 | 1.2 | 0 | 102.8571 | 20 | Irreparable damage to generator.
Unloader SDL1 | DS1 Slight | 0.3 | 0.5 | 0.06 | 1 | 5 | 1 | Minor deformation to rail support and unloader bracing frame elements.
Unloader SDL1 | DS2 Moderate | 0.5 | 0.6 | 0.2 | 0.6 | 17 | 4 | Significant deformation of unloader structural elements leading to misalignment of machine components and conveyors. Minor derailment from tracks on wharf. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2 as reference for moderate damage for 0.3g design level.
Unloader SDL1 | DS3 Extensive | 0.7 | 0.55 | 0.8 | 0.2 | 37 | 7 | Failure of bracing elements on unloader leading to permanent distortion of equipment. Damage to power supply and control equipment. Major derailment.
Unloader SDL1 | DS4 Complete | 0.9 | 0.46 | 1.2 | 0 | 77.1429 | 15 | Overturning with major distortion of structural elements.
Coal Yard SDL1 | DS1 Slight | 0.67 | 0.2 | 0.06 | 1 | 0.2 | 0.2 | Minor deformations in connections or hairline cracks in a few welds. Minor brace deformation. Some deformation at hold down bolts. | Wind dominance to effective desing resistance of 0.6g
Coal Yard SDL1 | DS2 Moderate | 0.85 | 0.27 | 0.3 | 1 | 1 | 0.5 | Some steel members have yielded exhibiting observable permanent rotations at connections. A few welded connections may exhibit major cracks through welds or a few bolted connections may exhibit broken bolts or enlarged bolt holes. Some yielding of braces and soem anchor bolts stretched.
Coal Yard SDL1 | DS3 Extensive | 1.05 | 0.35 | 0.75 | 0 | 1.5 | 1.5 | Many steel bracing elements have exceeded their yield capacity resulting in significant permanent lateral deformation of the structure. Many truss arch members have buckeld in compression. Some of the structural connections may have exceeded their ultimate capacity exhibited by major permanent member rotations at connections, buckled flanges and failed connections. Some foundation oviement due to settlement and some anchor bolts failed.
Coal Yard SDL1 | DS4 Complete | 1.35 | 0.35 | 1 | 0 | 3 | 3 | A significant proportion of the structural elements have exceeded their ultimate capacities or some critical structural elements or connections have failed resulting in dangerous permanent lateral displacement, partial collapse or collapse of the shelter structure.
Switch Yard | DS1 Slight | 0.11 | 0.7 | 0.3 | 1 | 1 | 0.5 |  | HAZUS-MH MR3 Table 8.22.a Substations
Switch Yard | DS2 Moderate | 0.15 | 0.75 | 0.6 | 0.6 | 3 | 1.5 |  | HAZUS-MH MR3 Table 8.22.a Substations
Switch Yard | DS3 Extensive | 0.2 | 0.75 | 0.8 | 0.2 | 7 | 3.5 |  | HAZUS-MH MR3 Table 8.22.a Substations
Switch Yard | DS4 Complete | 0.47 | 0.7 | 1 | 0 | 30 | 15 |  | HAZUS-MH MR3 Table 8.22.a Substations
SYSTEM_OUTPUT | DS1 Slight | 5 | 0.01 | 0.1 | 1 | 1 | 0.01
SYSTEM_OUTPUT | DS2 Moderate | 5 | 0.01 | 0.1 | 1 | 1 | 0.01
SYSTEM_OUTPUT | DS3 Extensive | 5 | 0.01 | 0.1 | 1 | 1 | 0.01
SYSTEM_OUTPUT | DS4 Complete | 5 | 0.01 | 1 | 1 | 1 | 0.01

## comp_type_dmg_algo 0.3g
Description: | List of component types with fragility and recovery data
Note: | Fragilities are defined according to discrete damage states. Recovery time is in WEEKS.
component_type | damage_state | damage_med | damage_logstd | damage_ratio | functionality | recovery_mean | recovery_std |  | Source
Ash Disposal System SDL2 | DS1 Slight | 0.39 | 0.2 | 0.05 | 1 | 0.2 | 0.5 | Minor deformation to supporting structure with some yielding of hold-down bolts. | SIM to mian feed conveyor
Ash Disposal System SDL2 | DS2 Moderate | 0.53 | 0.3 | 0.3 | 0 | 0.5 | 1.5 | Significant deformaton to steel supporting structure with misaligment of ash handling conveyors | SIM to mian feed conveyor
Ash Disposal System SDL2 | DS3 Extensive | 0.7 | 0.35 | 0.75 | 0 | 1 | 3.5 | Horizontal displacement of structure with failure of bracing elements and damage to ash silo structure. | SIM to mian feed conveyor
Ash Disposal System SDL2 | DS4 Complete | 0.95 | 0.35 | 1 | 0 | 4.2857 | 15 | Partial or complete collapse of ash handling system. | SIM to mian feed conveyor
Boiler SDL2 | DS1 Slight | 0.4 | 0.24 | 0.1 | 1 | 3 | 1 | Minor deformation to supporting structure and minor damage at lateral restraint points to boiler. No internal damage to boiler. | Using MH Hazus Table D8.8 for Boilers and pressue Vessels Anchored assuming HAZUS equivalent to 0.3g design level. Adjustments made to beat to reflect Mindoro Eqke outcomes.
Boiler SDL2 | DS2 Moderate | 0.52 | 0.26 | 0.3 | 0 | 20 | 4 | Significant deformation to supporting structure with deformation at holding down bolts and yielding of bracing elements. Damage to internal boiler pipes requiring access for repair.
Boiler SDL2 | DS3 Extensive | 0.75 | 0.35 | 0.9 | 0 | 60 | 10 | Major damage to boiler support with failure of many bracing elements. Large deformations damage connecting pipework. Widespread damage to internal steam pipes in boiler requring extensive replacement.
Boiler SDL2 | DS4 Complete | 1.8 | 0.6 | 1.3 | 0 | 102.8571 | 20 | Damage beyond repair
Turbine and Condenser SDL2 | DS1 Slight | 0.7 | 0.28 | 0.1 | 1 | 5 | 0.5 | Minor damage to condensor pipework. Some horizontal deformation of condensor support connections and steam supply to turbine.
Turbine and Condenser SDL2 | DS2 Moderate | 0.95 | 0.3 | 0.3 | 0 | 20 | 1.5 | Significant horizontal deformation of both condensor and turbine relative to supporting plinth leading to misalignment of turbine shaft to generator and steam leakage in pipework.
Turbine and Condenser SDL2 | DS3 Extensive | 1.28 | 0.34 | 0.85 | 0 | 50 | 3.5 | Large horizontal deformation of both condensor and turbine relative to supporting plinth leading to damage to turbine shaft to generator requiring replacement. Internal damage to condensor requiring replacement.
Turbine and Condenser SDL2 | DS4 Complete | 1.5 | 0.28 | 1.2 | 0 | 102.8571 | 15 | Irreparable damage to turbine and condensor.
Cooling System SDL2 | DS1 Slight | 0.37 | 0.4 | 0.1 | 1 | 1 | 0.5 | Minor damage to water handling pumps and pipework. Minor damage to pumphouse superstructure. | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
Cooling System SDL2 | DS2 Moderate | 0.52 | 0.4 | 0.3 | 0 | 3 | 1.5 | Moderate structural damage to pumphouse superstructure. Deformation of pump hold-down and pipework with some leakage at flanges and valves. Some movement of pumphouse substructure due to liquefaction. | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
Cooling System SDL2 | DS3 Extensive | 0.73 | 0.5 | 0.75 | 0 | 7 | 3.5 | Rupture of some water mains due to failure of supporting strucuture. Significant movement of pumps and motors leading to some misalignment. Extensive damage to pumphouse superstructure, power supply and control panels. Movement of pumphouse substructure and other valve chambers leading to damage to water mains. | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
Cooling System SDL2 | DS4 Complete | 1.28 | 0.5 | 1 | 0 | 30 | 15 | Damage beyond repair. | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
Demineralisation Plant SDL2 | DS1 Slight | 0.37 | 0.16 | 0.1 | 1 | 5 | 0.3 | Minor damage to water handling pumps and pipework. Minor damage to plant superstructure. | Using MH Hazus Table 8.4 Medium Water Treatment Plant Anchored assuming HAZUS equivalent to 0.3g design level. Adjustment made to beta to reflect Mindoro eqke outcomes.
Demineralisation Plant SDL2 | DS2 Moderate | 0.52 | 0.28 | 0.3 | 0 | 10 | 2.7 | Moderate structural damage to demin plant superstructure. Deformation of pump hold-down and pipework with some leakage at flanges and valves. Some movement of pumphouse substructure due to liquefaction.
Demineralisation Plant SDL2 | DS3 Extensive | 0.73 | 0.35 | 0.75 | 0 | 21 | 10 | Rupture of some water mains due to failure of supporting strucuture. Significant movement of pumps and motors leading to some misalignment. Extensive damage to demin plant superstructure, power supply and control panels. Movement of demin substructure and other valve chambers significant leading to damage to water mains.
Demineralisation Plant SDL2 | DS4 Complete | 1.28 | 0.4 | 1 | 0 | 42.8571 | 18 | Damage beyond repair.
Electrostatic Precipitator SDL2 | DS1 Slight | 0.3 | 0.4 | 0.1 | 1 | 5 | 0.5 | minor damage to supporting structure and electrical equipment | HAZUS-MH Table D8.8 Electircal equipment
Electrostatic Precipitator SDL2 | DS2 Moderate | 0.5 | 0.5 | 0.3 | 0 | 17 | 0.5 | significant deformation to supporting structure. Leakage of flue gases. Some damage to internal discharge electrodes and collector panels. | HAZUS-MH Table D8.8 Electircal equipment
Electrostatic Precipitator SDL2 | DS3 Extensive | 0.7 | 0.4 | 0.75 | 0 | 37 | 1.5 | Major deformation of supporting structure with failure of key bracing elements and permanent offset. Internal discharge electrodes and collector panels extensively damaged. Damage to high voltage power supply and control equipment. | Sim to main feed conveyor
Electrostatic Precipitator SDL2 | DS4 Complete | 0.95 | 0.4 | 1 | 0 | 77.1429 | 3 | Damage beyond repair. | Sim to main feed conveyor
Main Feed Conveyor SDL2 | DS1 Slight | 0.39 | 0.2 | 0.06 | 1 | 5 | 0.5 | Minor deformation of support structure with some yeilding of holding down bolts.
Main Feed Conveyor SDL2 | DS2 Moderate | 0.53 | 0.3 | 0.3 | 0 | 17 | 1.5 | Significant deformation of supporting structure with horizontal displacement of conveyor system. Misalignment of feed conveyors.
Main Feed Conveyor SDL2 | DS3 Extensive | 0.7 | 0.35 | 0.75 | 0 | 37 | 3.5 | Major damage to supporting structure with failure of bracing elelments. Damage to seating of conveyor structure on supporting frame. Possible permanent drift due to foundation settlement.
Main Feed Conveyor SDL2 | DS4 Complete | 0.95 | 0.35 | 1 | 0 | 77.1429 | 15 | Partial or complete collapse.
Fresh Water Source SDL2 | DS1 Slight | 0.37 | 0.16 | 0.1 | 1 | 1 | 0.2 | Minor movement of intake structure and minor damage to freshwater pumps and pipework. | Using MH Hazus Table 8.4 Medium Water Treatment Plant Anchored assuming HAZUS equivalent to 0.3g design level. Adjustment made to beta to reflect Mindoro eqke outcomes.
Fresh Water Source SDL2 | DS2 Moderate | 0.52 | 0.28 | 0.3 | 0 | 4 | 0.5 | Partial liquefaction of soils in the vicinity of intake structure leading to some horizontal movement and rotation with attendent damage to pipework. Horizontal movement to freshwater pumps and peripheral pipework.
Fresh Water Source SDL2 | DS3 Extensive | 0.73 | 0.35 | 0.75 | 0 | 8 | 1.5 | Extensive liquefaction leading to large scale movement of intake structures with major damage to both pipework and pumping facilities. Control equipment damaged.
Fresh Water Source SDL2 | DS4 Complete | 1.28 | 0.4 | 1 | 0 | 12 | 3 | Damage beyond repair
Power House SDL2 | DS1 Slight | 0.28 | 0.25 | 0.06 | 1 | 1 | 0.2 | Minor deformations in connections or hairline cracks in a few welds. Minor brace deformation. Minor spalling at some precast panel corners.
Power House SDL2 | DS2 Moderate | 0.43 | 0.35 | 0.3 | 1 | 4 | 0.5 | Some steel members have yielded exhibiting observable permanent rotations at connections. A few welded connections may exhibit major cracks through welds or a few bolted connections may exhibit broken bolts or enlarged bolt holes. Some yielding of braces. More significant spalling damage to precast panels with deformation at panel connections.
Power House SDL2 | DS3 Extensive | 0.6 | 0.4 | 0.75 | 0 | 8 | 1.5 | Most steel members have exceeded their yield capacity resulting in significant permanent lateral deformation of the structure. Some of the structural members or connections may have exceeded their ultimate capacity exhibited by major permanent member rotations at connections, buckled flanges and failed connections. Some anchor bolts stretched. Partial collapse of portions of the structure may have occurred due to failed critical elements or connections.
Power House SDL2 | DS4 Complete | 0.85 | 0.4 | 1 | 0 | 12 | 3 | A significant proportion of the structural elements have exceeded their ultimate capacities or some critical structural elements or connections have failed resulting in dangerous permanent lateral displacement, partial collapse or collapse of the building.
Stack SDL2 | DS1 Slight | 0.67 | 0.2 | 0.1 | 1 | 5 | 0.5 | Minor damage to structure with deformation of holding down bolts and with some bracing connections.
Stack SDL2 | DS2 Moderate | 0.85 | 0.27 | 0.4 | 0 | 17 | 1.5 | Significant deformation of supporting structure with horizontal displacement. Yielding of bracing elements. Damage to flue leading to gas leakage.
Stack SDL2 | DS3 Extensive | 1.05 | 0.35 | 0.8 | 0 | 37 | 3.5 | Major horizontal deformation with permanent drift. Failure of bracing elements and extensive damage to flue with many leakage points.
Stack SDL2 | DS4 Complete | 1.35 | 0.35 | 1.2 | 0 | 77.1429 | 15 | Damage beyond repair including collapse.
Stacker Reclaimer SDL2 | DS1 Slight | 0.38 | 0.6 | 0.06 | 1 | 5 | 0.5 | Minor deformation to rail support and stacker reclaimer bracing elements. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Stacker Reclaimer SDL2 | DS2 Moderate | 0.59 | 0.62 | 0.2 | 0 | 17 | 1.5 | Significant deformation of stacker structural elements leading to misalignment of machine components and conveyors. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Stacker Reclaimer SDL2 | DS3 Extensive | 0.79 | 0.64 | 0.8 | 0 | 37 | 3.5 | Ground deformation leading to gross movement of support rails. Failure of bracing elements on stacker leading to permanent distortion of equipment. Damage to power supply and control equipment. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Stacker Reclaimer SDL2 | DS4 Complete | 1 | 0.55 | 1.2 | 0 | 77.1429 | 15 | Overturning with major distortion of structural elements. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Stepup Transformer SDL2 | DS1 Slight | 0.5 | 0.36 | 0.03 | 1 | 5 | 0.5 | Porcelain Gasket Leak | Assume Syner G Table 3.22 230kV with Anchored Sub Components
Stepup Transformer SDL2 | DS2 Moderate | 0.85 | 0.28 | 0.1 | 0 | 17 | 1.5 | Porcelain Break, Major break in Radiator | Assume Syner G Table 3.22 230kV with Anchored Sub Components
Stepup Transformer SDL2 | DS3 Extensive | 1.2 | 0.23 | 0.15 | 0 | 37 | 3.5 | Anchorage Failure | Assume Syner G Table 3.22 230kV with Anchored Sub Components
Stepup Transformer SDL2 | DS4 Complete | 1.6 | 0.13 | 1 | 0 | 77.1429 | 15 | Overturn | Assume Syner G Table 3.22 230kV with Anchored Sub Components
Supply Conveyor SDL2 | DS1 Slight | 0.3 | 0.28 | 0.1 | 1 | 5 | 0.5 | Minor deformation of support structure with some yeilding of holding down bolts.
Supply Conveyor SDL2 | DS2 Moderate | 0.45 | 0.36 | 0.4 | 1 | 17 | 1.5 | Significant deformation of supporting structure with horizontal displacement of conveyor system. Misalignment of feed conveyors.
Supply Conveyor SDL2 | DS3 Extensive | 0.65 | 0.45 | 0.8 | 0 | 37 | 3.5 | Major damage to supporting structure with failure of bracing elelments. Damage to seating of conveyor structure on supporting frame. Possible permanent drift due to foundation settlement.
Supply Conveyor SDL2 | DS4 Complete | 0.95 | 0.45 | 1 | 0 | 77.1429 | 15 | Partial or complete collapse.
Generator SDL2 | DS1 Slight | 0.7 | 0.28 | 0.03 | 1 | 3 | 1 | Minor damage to generator electrical connectivity. Some horizonrtal deformation to generator support with distortion of holding down bolts. | HAZUS-MH MR3 Table 8.22.a Generation Facilities
Generator SDL2 | DS2 Moderate | 0.95 | 0.3 | 0.15 | 0 | 20 | 4 | Significant horizontal deformation leading to misalignment of generator to turbine shaft. | HAZUS-MH MR3 Table 8.22.a Generation Facilities
Generator SDL2 | DS3 Extensive | 1.28 | 0.34 | 0.4 | 0 | 60 | 10 | Large horizontal deformation of both condensor and turbine relative to supporting plinth leading to damage to generator to turbine shaft requiring replacement. | HAZUS-MH MR3 Table 8.22.a Generation Facilities
Generator SDL2 | DS4 Complete | 1.5 | 0.28 | 1.2 | 0 | 102.8571 | 20 | Irreparable damage to generator. | HAZUS-MH MR3 Table 8.22.a Generation Facilities
Unloader SDL2 | DS1 Slight | 0.38 | 0.6 | 0.06 | 1 | 5 | 1 | Minor deformation to rail support and unloader bracing frame elements. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Unloader SDL2 | DS2 Moderate | 0.59 | 0.62 | 0.2 | 0.6 | 17 | 4 | Significant deformation of unloader structural elements leading to misalignment of machine components and conveyors. Minor derailment from tracks on wharf. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Unloader SDL2 | DS3 Extensive | 0.79 | 0.64 | 0.8 | 0.2 | 37 | 7 | Failure of bracing elements on unloader leading to permanent distortion of equipment. Damage to power supply and control equipment. Major derailment. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Unloader SDL2 | DS4 Complete | 1 | 0.55 | 1.2 | 0 | 77.1429 | 15 | Overturning with major distortion of structural elements. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Coal Yard SDL2 | DS1 Slight | 0.67 | 0.2 | 0.06 | 1 | 0.2 | 0.2 | Minor deformations in connections or hairline cracks in a few welds. Minor brace deformation. Some deformation at hold down bolts.
Coal Yard SDL2 | DS2 Moderate | 0.85 | 0.27 | 0.3 | 1 | 1 | 0.5 | Some steel members have yielded exhibiting observable permanent rotations at connections. A few welded connections may exhibit major cracks through welds or a few bolted connections may exhibit broken bolts or enlarged bolt holes. Some yielding of braces and soem anchor bolts stretched.
Coal Yard SDL2 | DS3 Extensive | 1.05 | 0.35 | 0.75 | 0 | 1.5 | 1.5 | Many steel bracing elements have exceeded their yield capacity resulting in significant permanent lateral deformation of the structure. Many truss arch members have buckeld in compression. Some of the structural connections may have exceeded their ultimate capacity exhibited by major permanent member rotations at connections, buckled flanges and failed connections. Some foundation oviement due to settlement and some anchor bolts failed.
Coal Yard SDL2 | DS4 Complete | 1.35 | 0.35 | 1 | 0 | 3 | 3 | A significant proportion of the structural elements have exceeded their ultimate capacities or some critical structural elements or connections have failed resulting in dangerous permanent lateral displacement, partial collapse or collapse of the shelter structure.
Switch Yard | DS1 Slight | 0.11 | 0.7 | 0.3 | 1 | 1 | 0.5 |  | HAZUS-MH MR3 Table 8.22.a Substations
Switch Yard | DS2 Moderate | 0.15 | 0.75 | 0.6 | 0.6 | 3 | 1.5 |  | HAZUS-MH MR3 Table 8.22.a Substations
Switch Yard | DS3 Extensive | 0.2 | 0.75 | 0.8 | 0.2 | 7 | 3.5 |  | HAZUS-MH MR3 Table 8.22.a Substations
Switch Yard | DS4 Complete | 0.47 | 0.7 | 1 | 0 | 30 | 15 |  | HAZUS-MH MR3 Table 8.22.a Substations
SYSTEM_OUTPUT | DS1 Slight | 5 | 0.01 | 0.1 | 1 | 1 | 0.01
SYSTEM_OUTPUT | DS2 Moderate | 5 | 0.01 | 0.1 | 1 | 1 | 0.01
SYSTEM_OUTPUT | DS3 Extensive | 5 | 0.01 | 0.1 | 1 | 1 | 0.01
SYSTEM_OUTPUT | DS4 Complete | 5 | 0.01 | 1 | 1 | 1 | 0.01

## comp_type_dmg_algo 0.4g
Description: | List of component types with fragility and recovery data
Note: | Fragilities are defined according to discrete damage states. Recovery time is in WEEKS.
component_type | damage_state | damage_med | damage_logstd | damage_ratio | functionality | recovery_mean | recovery_std |  | Source
Ash Disposal System SDL3 | DS1 Slight | 0.37 | 0.27 | 0.05 | 1 | 0.2 | 0.5 | Minor deformation to supporting structure with some yielding of hold-down bolts. | SIM to supply conveyor
Ash Disposal System SDL3 | DS2 Moderate | 0.55 | 0.32 | 0.3 | 0 | 0.5 | 1.5 | Significant deformaton to steel supporting structure with misaligment of ash handling conveyors | SIM to supply conveyor
Ash Disposal System SDL3 | DS3 Extensive | 0.75 | 0.42 | 0.75 | 0 | 1 | 3.5 | Horizontal displacement of structure with failure of bracing elements and damage to ash silo structure. | SIM to supply conveyor
Ash Disposal System SDL3 | DS4 Complete | 1.05 | 0.46 | 1 | 0 | 4.2857 | 15 | Partial or complete collapse of ash handling system. | SIM to supply conveyor
Boiler SDL3 | DS1 Slight | 0.4 | 0.55 | 0.1 | 1 | 3 | 1 | Minor deformation to supporting structure and minor damage at lateral restraint points to boiler. No internal damage to boiler.
Boiler SDL3 | DS2 Moderate | 0.62 | 0.65 | 0.3 | 0 | 20 | 4 | Significant deformation to supporting structure with deformation at holding down bolts and yielding of bracing elements. Damage to internal boiler pipes requiring access for repair.
Boiler SDL3 | DS3 Extensive | 0.95 | 0.6 | 0.9 | 0 | 60 | 10 | Major damage to boiler support with failure of many bracing elements. Large deformations damage connecting pipework. Widespread damage to internal steam pipes in boiler requring extensive replacement.
Boiler SDL3 | DS4 Complete | 1.9 | 0.65 | 1.3 | 0 | 102.8571 | 20 | Damage beyond repair
Turbine and Condenser SDL3 | DS1 Slight | 0.8 | 0.28 | 0.1 | 1 | 5 | 0.5 | Minor damage to condensor pipework. Some horizontal deformation of condensor support connections and steam supply to turbine.
Turbine and Condenser SDL3 | DS2 Moderate | 1.05 | 0.3 | 0.3 | 0 | 20 | 1.5 | Significant horizontal deformation of both condensor and turbine relative to supporting plinth leading to misalignment of turbine shaft to generator and steam leakage in pipework.
Turbine and Condenser SDL3 | DS3 Extensive | 1.38 | 0.34 | 0.85 | 0 | 50 | 3.5 | Large horizontal deformation of both condensor and turbine relative to supporting plinth leading to damage to turbine shaft to generator requiring replacement. Internal damage to condensor requiring replacement.
Turbine and Condenser SDL3 | DS4 Complete | 1.6 | 0.28 | 1.2 | 0 | 102.8571 | 15 | Irreparable damage to turbine and condensor.
Cooling System SDL3 | DS1 Slight | 0.47 | 0.35 | 0.1 | 1 | 1 | 0.5 | Minor damage to water handling pumps and pipework. Minor damage to pumphouse superstructure. | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
Cooling System SDL3 | DS2 Moderate | 0.62 | 0.35 | 0.3 | 0 | 3 | 1.5 | Moderate structural damage to pumphouse superstructure. Deformation of pump hold-down and pipework with some leakage at flanges and valves. Some movement of pumphouse substructure due to liquefaction. | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
Cooling System SDL3 | DS3 Extensive | 0.83 | 0.45 | 0.75 | 0 | 7 | 3.5 | Rupture of some water mains due to failure of supporting strucuture. Significant movement of pumps and motors leading to some misalignment. Extensive damage to pumphouse superstructure, power supply and control panels. Movement of pumphouse substructure and other valve chambers leading to damage to water mains. | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
Cooling System SDL3 | DS4 Complete | 1.38 | 0.45 | 1 | 0 | 30 | 15 | Damage beyond repair. | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
Demineralisation Plant SDL3 | DS1 Slight | 0.35 | 0.5 | 0.1 | 1 | 5 | 0.3 | Minor damage to water handling pumps and pipework. Minor damage to plant superstructure. | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
Demineralisation Plant SDL3 | DS2 Moderate | 0.48 | 0.5 | 0.3 | 0 | 10 | 2.7 | Moderate structural damage to demin plant superstructure. Deformation of pump hold-down and pipework with some leakage at flanges and valves. Some movement of pumphouse substructure due to liquefaction. | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
Demineralisation Plant SDL3 | DS3 Extensive | 0.63 | 0.6 | 0.75 | 0 | 21 | 10 | Rupture of some water mains due to failure of supporting strucuture. Significant movement of pumps and motors leading to some misalignment. Extensive damage to demin plant superstructure, power supply and control panels. Movement of demin substructure and other valve chambers significant leading to damage to water mains. | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
Demineralisation Plant SDL3 | DS4 Complete | 0.93 | 0.6 | 1 | 0 | 42.8571 | 18 | Damage beyond repair. | HAZUS-MH MR3 Table 8.3 Small Water Treatment Plants
Electrostatic Precipitator SDL3 | DS1 Slight | 0.35 | 0.5 | 0.1 | 1 | 5 | 0.5 | minor damage to supporting structure and electrical equipment | HAZUS-MH Table D8.8 Electircal equipment
Electrostatic Precipitator SDL3 | DS2 Moderate | 0.48 | 0.5 | 0.3 | 0 | 17 | 0.5 | significant deformation to supporting structure. Leakage of flue gases. Some damage to internal discharge electrodes and collector panels. | HAZUS-MH Table D8.8 Electircal equipment
Electrostatic Precipitator SDL3 | DS3 Extensive | 0.63 | 0.6 | 0.75 | 0 | 37 | 1.5 | Major deformation of supporting structure with failure of key bracing elements and permanent offset. Internal discharge electrodes and collector panels extensively damaged. Damage to high voltage power supply and control equipment. | Sim to main feed conveyor
Electrostatic Precipitator SDL3 | DS4 Complete | 0.93 | 0.6 | 1 | 0 | 77.1429 | 3 | Damage beyond repair. | Sim to main feed conveyor
Main Feed Conveyor SDL3 | DS1 Slight | 0.37 | 0.21 | 0.06 | 1 | 5 | 0.5 | Minor deformation of support structure with some yeilding of holding down bolts.
Main Feed Conveyor SDL3 | DS2 Moderate | 0.55 | 0.26 | 0.3 | 0 | 17 | 1.5 | Significant deformation of supporting structure with horizontal displacement of conveyor system. Misalignment of feed conveyors.
Main Feed Conveyor SDL3 | DS3 Extensive | 0.75 | 0.36 | 0.75 | 0 | 37 | 3.5 | Major damage to supporting structure with failure of bracing elelments. Damage to seating of conveyor structure on supporting frame. Possible permanent drift due to foundation settlement.
Main Feed Conveyor SDL3 | DS4 Complete | 1.05 | 0.4 | 1 | 0 | 77.1429 | 15 | Partial or complete collapse.
Fresh Water Source SDL3 | DS1 Slight | 0.25 | 0.7 | 0.1 | 1 | 1 | 0.2 | Minor movement of intake structure and minor damage to freshwater pumps and pipework. | HAZUS-MH MR3 Table 8.6 Small Pumping Plants
Fresh Water Source SDL3 | DS2 Moderate | 0.46 | 0.65 | 0.3 | 0 | 4 | 0.5 | Partial liquefaction of soils in the vicinity of intake structure leading to some horizontal movement and rotation with attendent damage to pipework. Horizontal movement to freshwater pumps and peripheral pipework.
Fresh Water Source SDL3 | DS3 Extensive | 0.76 | 0.65 | 0.75 | 0 | 8 | 1.5 | Extensive liquefaction leading to large scale movement of intake structures with major damage to both pipework and pumping facilities. Control equipment damaged.
Fresh Water Source SDL3 | DS4 Complete | 1.6 | 0.8 | 1 | 0 | 12 | 3 | Damage beyond repair
Power House SDL3 | DS1 Slight | 0.27 | 0.25 | 0.06 | 1 | 1 | 0.2 | Minor deformations in connections or hairline cracks in a few welds. Minor brace deformation. Minor spalling at some precast panel corners.
Power House SDL3 | DS2 Moderate | 0.45 | 0.32 | 0.3 | 1 | 4 | 0.5 | Some steel members have yielded exhibiting observable permanent rotations at connections. A few welded connections may exhibit major cracks through welds or a few bolted connections may exhibit broken bolts or enlarged bolt holes. Some yielding of braces. More significant spalling damage to precast panels with deformation at panel connections.
Power House SDL3 | DS3 Extensive | 0.65 | 0.4 | 0.75 | 0 | 8 | 1.5 | Most steel members have exceeded their yield capacity resulting in significant permanent lateral deformation of the structure. Some of the structural members or connections may have exceeded their ultimate capacity exhibited by major permanent member rotations at connections, buckled flanges and failed connections. Some anchor bolts stretched. Partial collapse of portions of the structure may have occurred due to failed critical elements or connections.
Power House SDL3 | DS4 Complete | 0.95 | 0.4 | 1 | 0 | 12 | 3 | A significant proportion of the structural elements have exceeded their ultimate capacities or some critical structural elements or connections have failed resulting in dangerous permanent lateral displacement, partial collapse or collapse of the building.
Stack SDL3 | DS1 Slight | 0.67 | 0.2 | 0.1 | 1 | 5 | 0.5 | Minor damage to structure with deformation of holding down bolts and with some bracing connections.
Stack SDL3 | DS2 Moderate | 0.85 | 0.27 | 0.4 | 0 | 17 | 1.5 | Significant deformation of supporting structure with horizontal displacement. Yielding of bracing elements. Damage to flue leading to gas leakage.
Stack SDL3 | DS3 Extensive | 1.05 | 0.35 | 0.8 | 0 | 37 | 3.5 | Major horizontal deformation with permanent drift. Failure of bracing elements and extensive damage to flue with many leakage points.
Stack SDL3 | DS4 Complete | 1.35 | 0.35 | 1.2 | 0 | 77.1429 | 15 | Damage beyond repair including collapse.
Stacker Reclaimer SDL3 | DS1 Slight | 0.4 | 0.5 | 0.06 | 1 | 5 | 0.5 | Minor deformation to rail support and stacker reclaimer bracing elements. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Stacker Reclaimer SDL3 | DS2 Moderate | 0.6 | 0.6 | 0.2 | 0 | 17 | 1.5 | Significant deformation of stacker structural elements leading to misalignment of machine components and conveyors. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Stacker Reclaimer SDL3 | DS3 Extensive | 0.8 | 0.55 | 0.8 | 0 | 37 | 3.5 | Ground deformation leading to gross movement of support rails. Failure of bracing elements on stacker leading to permanent distortion of equipment. Damage to power supply and control equipment. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Stacker Reclaimer SDL3 | DS4 Complete | 1 | 0.46 | 1.2 | 0 | 77.1429 | 15 | Overturning with major distortion of structural elements. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Stepup Transformer SDL3 | DS1 Slight | 0.6 | 0.32 | 0.03 | 1 | 5 | 0.5 | Porcelain Gasket Leak | Assume Syner G Table 3.22 230kV with Anchored Sub Components
Stepup Transformer SDL3 | DS2 Moderate | 0.95 | 0.24 | 0.1 | 0 | 17 | 1.5 | Porcelain Break, Major break in Radiator | Assume Syner G Table 3.22 230kV with Anchored Sub Components
Stepup Transformer SDL3 | DS3 Extensive | 1.3 | 0.19 | 0.15 | 0 | 37 | 3.5 | Anchorage Failure | Assume Syner G Table 3.22 230kV with Anchored Sub Components
Stepup Transformer SDL3 | DS4 Complete | 1.7 | 0.09 | 1 | 0 | 77.1429 | 15 | Overturn | Assume Syner G Table 3.22 230kV with Anchored Sub Components
Supply Conveyor SDL3 | DS1 Slight | 0.37 | 0.27 | 0.1 | 1 | 5 | 0.5 | Minor deformation of support structure with some yeilding of holding down bolts.
Supply Conveyor SDL3 | DS2 Moderate | 0.55 | 0.32 | 0.4 | 1 | 17 | 1.5 | Significant deformation of supporting structure with horizontal displacement of conveyor system. Misalignment of feed conveyors.
Supply Conveyor SDL3 | DS3 Extensive | 0.85 | 0.42 | 0.8 | 0 | 37 | 3.5 | Major damage to supporting structure with failure of bracing elelments. Damage to seating of conveyor structure on supporting frame. Possible permanent drift due to foundation settlement.
Supply Conveyor SDL3 | DS4 Complete | 1.05 | 0.46 | 1 | 0 | 77.1429 | 15 | Partial or complete collapse.
Generator SDL3 | DS1 Slight | 0.8 | 0.28 | 0.03 | 1 | 3 | 1 | Minor damage to generator electrical connectivity. Some horizonrtal deformation to generator support with distortion of holding down bolts. | HAZUS-MH MR3 Table 8.22.a Generation Facilities
Generator SDL3 | DS2 Moderate | 1.05 | 0.3 | 0.15 | 0 | 20 | 4 | Significant horizontal deformation leading to misalignment of generator to turbine shaft. | HAZUS-MH MR3 Table 8.22.a Generation Facilities
Generator SDL3 | DS3 Extensive | 1.38 | 0.34 | 0.4 | 0 | 60 | 10 | Large horizontal deformation of both condensor and turbine relative to supporting plinth leading to damage to generator to turbine shaft requiring replacement. | HAZUS-MH MR3 Table 8.22.a Generation Facilities
Generator SDL3 | DS4 Complete | 1.6 | 0.28 | 1.2 | 0 | 102.8571 | 20 | Irreparable damage to generator. | HAZUS-MH MR3 Table 8.22.a Generation Facilities
Unloader SDL3 | DS1 Slight | 0.5 | 0.5 | 0.06 | 1 | 5 | 1 | Minor deformation to rail support and unloader bracing frame elements. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Unloader SDL3 | DS2 Moderate | 0.7 | 0.6 | 0.2 | 0.6 | 17 | 4 | Significant deformation of unloader structural elements leading to misalignment of machine components and conveyors. Minor derailment from tracks on wharf. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Unloader SDL3 | DS3 Extensive | 0.9 | 0.55 | 0.8 | 0.2 | 37 | 7 | Failure of bracing elements on unloader leading to permanent distortion of equipment. Damage to power supply and control equipment. Major derailment. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Unloader SDL3 | DS4 Complete | 1.1 | 0.46 | 1.2 | 0 | 77.1429 | 15 | Overturning with major distortion of structural elements. | Assume unanchored refinery electrical/mechanical equipment MH HAZUS Table C8.2
Coal Yard SDL3 | DS1 Slight | 0.67 | 0.2 | 0.06 | 1 | 0.2 | 0.2 | Minor deformations in connections or hairline cracks in a few welds. Minor brace deformation. Some deformation at hold down bolts.
Coal Yard SDL3 | DS2 Moderate | 0.85 | 0.27 | 0.3 | 1 | 1 | 0.5 | Some steel members have yielded exhibiting observable permanent rotations at connections. A few welded connections may exhibit major cracks through welds or a few bolted connections may exhibit broken bolts or enlarged bolt holes. Some yielding of braces and soem anchor bolts stretched.
Coal Yard SDL3 | DS3 Extensive | 1.05 | 0.35 | 0.75 | 0 | 1.5 | 1.5 | Many steel bracing elements have exceeded their yield capacity resulting in significant permanent lateral deformation of the structure. Many truss arch members have buckeld in compression. Some of the structural connections may have exceeded their ultimate capacity exhibited by major permanent member rotations at connections, buckled flanges and failed connections. Some foundation oviement due to settlement and some anchor bolts failed.
Coal Yard SDL3 | DS4 Complete | 1.35 | 0.35 | 1 | 0 | 3 | 3 | A significant proportion of the structural elements have exceeded their ultimate capacities or some critical structural elements or connections have failed resulting in dangerous permanent lateral displacement, partial collapse or collapse of the shelter structure.
Switch Yard | DS1 Slight | 0.11 | 0.7 | 0.3 | 1 | 1 | 0.5 |  | HAZUS-MH MR3 Table 8.22.a Substations
Switch Yard | DS2 Moderate | 0.15 | 0.75 | 0.6 | 0.6 | 3 | 1.5 |  | HAZUS-MH MR3 Table 8.22.a Substations
Switch Yard | DS3 Extensive | 0.2 | 0.75 | 0.8 | 0.2 | 7 | 3.5 |  | HAZUS-MH MR3 Table 8.22.a Substations
Switch Yard | DS4 Complete | 0.47 | 0.7 | 1 | 0 | 30 | 15 |  | HAZUS-MH MR3 Table 8.22.a Substations
SYSTEM_OUTPUT | DS1 Slight | 5 | 0.01 | 0.1 | 1 | 1 | 0.01
SYSTEM_OUTPUT | DS2 Moderate | 5 | 0.01 | 0.1 | 1 | 1 | 0.01
SYSTEM_OUTPUT | DS3 Extensive | 5 | 0.01 | 0.1 | 1 | 1 | 0.01
SYSTEM_OUTPUT | DS4 Complete | 5 | 0.01 | 1 | 1 | 1 | 0.01