## component_list
Description: | This file lists the instances of various component types within the system. Component design level x.xx g.
Note: | Cost fractions define economic value of the individual component relative to the cost of entire system. Data includes a 3% allowance for components not included in the model.
component_id | component_type | component_class | cost_fraction | node_type | node_cluster | op_capacity
commercial_power_supply | Electric Power Commercial | Energy Source | 0.02 | supply | Supply | 1
backup_power_supply | Electric Power Backup | Energy Source | 0.04 | supply | Supply | 1
well_1 | Wells | Water Supply | 0.041 | supply | Supply | 1
well_2 | Wells | Water Supply | 0.041 | supply | Supply | 1
feed_pump | Vertical Pump | Water Supply | 0.0025 | transshipment | Supply | 1
input_pipe_1 | Internal Pipework | Water Supply Pipe | 0.0025 | transshipment | Supply | 1
chem_tank_ph_acid | Chemical Tanks | Chem Dosage Stage 1 | 0.033 | dependency | none | 1
chem_tank_coag1 | Chemical Tanks | Chem Dosage Stage 1 | 0.033 | dependency | none | 1
pipe_fb_1 | Internal Pipework | Coagulation and Flocculation Inlets | 0.0025 | transshipment | Coagulation and Flocculation Inlets | 1
pipe_fb_2 | Internal Pipework | Coagulation and Flocculation Inlets | 0.0025 | transshipment | Coagulation and Flocculation Inlets | 1
pipe_fb_3 | Internal Pipework | Coagulation and Flocculation Inlets | 0.0025 | transshipment | Coagulation and Flocculation Inlets | 1
pipe_fb_4 | Internal Pipework | Coagulation and Flocculation Inlets | 0.0025 | transshipment | Coagulation and Flocculation Inlets | 1
pipe_fb_5 | Internal Pipework | Coagulation and Flocculation Inlets | 0.0025 | transshipment | Coagulation and Flocculation Inlets | 1
pipe_fb_6 | Internal Pipework | Coagulation and Flocculation Inlets | 0.0025 | transshipment | Coagulation and Flocculation Inlets | 1
pipe_fb_7 | Internal Pipework | Coagulation and Flocculation Inlets | 0.0025 | transshipment | Coagulation and Flocculation Inlets | 1
pipe_fb_8 | Internal Pipework | Coagulation and Flocculation Inlets | 0.0025 | transshipment | Coagulation and Flocculation Inlets | 1
floc_basin_1 | Sediment Flocculation | Coagulation and Flocculation | 0.0075 | transshipment | Coagulation and Flocculation | 1
floc_basin_2 | Sediment Flocculation | Coagulation and Flocculation | 0.0075 | transshipment | Coagulation and Flocculation | 1
floc_basin_3 | Sediment Flocculation | Coagulation and Flocculation | 0.0075 | transshipment | Coagulation and Flocculation | 1
floc_basin_4 | Sediment Flocculation | Coagulation and Flocculation | 0.0075 | transshipment | Coagulation and Flocculation | 1
floc_basin_5 | Sediment Flocculation | Coagulation and Flocculation | 0.0075 | transshipment | Coagulation and Flocculation | 1
floc_basin_6 | Sediment Flocculation | Coagulation and Flocculation | 0.0075 | transshipment | Coagulation and Flocculation | 1
floc_basin_7 | Sediment Flocculation | Coagulation and Flocculation | 0.0075 | transshipment | Coagulation and Flocculation | 1
floc_basin_8 | Sediment Flocculation | Coagulation and Flocculation | 0.0075 | transshipment | Coagulation and Flocculation | 1
pump_daf | Horizontal Pump | DAF Connector and Pump | 0.005 | dependency | none | 1
daf_1 | Basins | Dissolved Air Flotation | 0.0075 | transshipment | Dissolved Air Flotation | 1
daf_2 | Basins | Dissolved Air Flotation | 0.0075 | transshipment | Dissolved Air Flotation | 1
daf_3 | Basins | Dissolved Air Flotation | 0.0075 | transshipment | Dissolved Air Flotation | 1
daf_4 | Basins | Dissolved Air Flotation | 0.0075 | transshipment | Dissolved Air Flotation | 1
daf_5 | Basins | Dissolved Air Flotation | 0.0075 | transshipment | Dissolved Air Flotation | 1
daf_6 | Basins | Dissolved Air Flotation | 0.0075 | transshipment | Dissolved Air Flotation | 1
daf_7 | Basins | Dissolved Air Flotation | 0.0075 | transshipment | Dissolved Air Flotation | 1
daf_8 | Basins | Dissolved Air Flotation | 0.0075 | transshipment | Dissolved Air Flotation | 1
connector_daf | Pipe Connectors | DAF Connector and Pump | 0.0025 | transshipment | DAF Connector | 1
pipe_oz_1 | Internal Pipework | Ozone Disinfection Pipework | 0.0025 | transshipment | Ozone Disinfection Pipework | 1
pipe_oz_2 | Internal Pipework | Ozone Disinfection Pipework | 0.0025 | transshipment | Ozone Disinfection Pipework | 1
ozone_gen | Chemical Tanks | Ozone Disinfection | 0.0025 | dependency | Ozone Disinfection | 1
ozone_contact_1 | Basins | Ozone Disinfection | 0.025 | transshipment | Ozone Disinfection | 1
ozone_contact_2 | Basins | Ozone Disinfection | 0.025 | transshipment | Ozone Disinfection | 1
connector_oz | Pipe Connectors | Ozone Disinfection Connector | 0.0025 | transshipment | Ozone Disinfection Connector | 1
pipe_ft_1 | Internal Pipework | Filtration Inlet Pipework | 0.0025 | transshipment | Filtration Inlet Pipework | 1
pipe_ft_2 | Internal Pipework | Filtration Inlet Pipework | 0.0025 | transshipment | Filtration Inlet Pipework | 1
pipe_ft_3 | Internal Pipework | Filtration Inlet Pipework | 0.0025 | transshipment | Filtration Inlet Pipework | 1
pipe_ft_4 | Internal Pipework | Filtration Inlet Pipework | 0.0025 | transshipment | Filtration Inlet Pipework | 1
pipe_ft_5 | Internal Pipework | Filtration Inlet Pipework | 0.0025 | transshipment | Filtration Inlet Pipework | 1
pipe_ft_6 | Internal Pipework | Filtration Inlet Pipework | 0.0025 | transshipment | Filtration Inlet Pipework | 1
pipe_ft_7 | Internal Pipework | Filtration Inlet Pipework | 0.0025 | transshipment | Filtration Inlet Pipework | 1
pipe_ft_8 | Internal Pipework | Filtration Inlet Pipework | 0.0025 | transshipment | Filtration Inlet Pipework | 1
filter_tank_1 | Basins | Filtration Tanks | 0.025 | transshipment | Filtration Tanks | 1
filter_tank_2 | Basins | Filtration Tanks | 0.025 | transshipment | Filtration Tanks | 1
filter_tank_3 | Basins | Filtration Tanks | 0.025 | transshipment | Filtration Tanks | 1
filter_tank_4 | Basins | Filtration Tanks | 0.025 | transshipment | Filtration Tanks | 1
filter_tank_5 | Basins | Filtration Tanks | 0.025 | transshipment | Filtration Tanks | 1
filter_tank_6 | Basins | Filtration Tanks | 0.025 | transshipment | Filtration Tanks | 1
filter_tank_7 | Basins | Filtration Tanks | 0.025 | transshipment | Filtration Tanks | 1
filter_tank_8 | Basins | Filtration Tanks | 0.025 | transshipment | Filtration Tanks | 1
pipe_ft_out_1 | Internal Pipework | Filtration Output Pipework | 0.0025 | transshipment | Filtration Ouput Pipework | 1
pipe_ccc_1 | Internal Pipework | Chlorine Disinfection Pipework | 0.0025 | transshipment | Chlorine Disinfection Pipework | 1
chlorine_tank | Chemical Tanks | Chlorine Disinfection | 0.033 | dependency | Chlorine Disinfection | 1
chem_tank_ph_base | Chemical Tanks | Chlorine Disinfection | 0.033 | dependency | Chlorine Disinfection | 1
chlorine_contact_chamber | Basins | Chlorine Disinfection | 0.0025 | transshipment | Chlorine Disinfection | 1
pipe_to_clearwell | Internal Pipework | Settling | 0.0025 | transshipment | Clearwell Input Pipework | 1
connector_clearwell | Pipe Connectors | Settling | 0.0025 | transshipment | Clearwell Input Connector | 1
clearwell_1 | Basins | Reservoir | 0.0025 | transshipment | Clearwell | 1
clearwell_2 | Basins | Reservoir | 0.0025 | transshipment | Clearwell | 1
pipe_cw_out_1 | Internal Pipework | Reticulation | 0.0025 | transshipment | Clearwell Output Pipe | 1
pipe_cw_out_2 | Internal Pipework | Reticulation | 0.0025 | transshipment | Clearwell Output Pipe | 1
pipe_connector_cw | Pipe Connectors | Reticulation | 0.0025 | transshipment | Clearwell Output Connector | 1
pipe_uv_in_1 | Internal Pipework | UV Disinfection Input | 0.0025 | transshipment | UV Disinfection Input | 1
pipe_uv_in_2 | Internal Pipework | UV Disinfection Input | 0.0025 | transshipment | UV Disinfection Input | 1
uv_chamber_1 | Basins | UV Disinfection | 0.025 | transshipment | UV Disinfection | 1
uv_chamber_2 | Basins | UV Disinfection | 0.025 | transshipment | UV Disinfection | 1
uv_chamber_3 | Basins | UV Disinfection | 0.025 | transshipment | UV Disinfection | 1
uv_chamber_4 | Basins | UV Disinfection | 0.025 | transshipment | UV Disinfection | 1
uv_chamber_5 | Basins | UV Disinfection | 0.025 | transshipment | UV Disinfection | 1
uv_chamber_6 | Basins | UV Disinfection | 0.025 | transshipment | UV Disinfection | 1
pipe_connector_uv_out | Pipe Connectors | UV Disinfection Output | 0.0025 | transshipment | UV Disinfection Output | 1
pipe_large_fl_1 | Internal Pipework | Water Conditioning | 0.0035 | transshipment | Water Conditioning | 1
pipe_large_fl_2 | Internal Pipework | Water Conditioning | 0.0035 | transshipment | Water Conditioning | 1
chem_tank_Fl | Chemical Tanks | Water Conditioning | 0.033 | dependency | none | 1
chem_tank_phosphate | Chemical Tanks | Water Conditioning | 0.033 | dependency | none | 1
pipe_to_distro_1 | Elevated Pipes | Supply to Distribution | 0.004 | transshipment | Supply to Distribution | 1
pipe_to_distro_2 | Elevated Pipes | Supply to Distribution | 0.004 | transshipment | Supply to Distribution | 1
output_1 | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | OUTPUT | 1
output_2 | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | OUTPUT | 1

## component_connections
Description: | Network connections. Each pair of nodes implies a connecting edge. Directionality is defined by order of nodes in a row (Orig -> Dest).
Note: | Used by: (1) network algorithm package for flow calculations, (2) Pygraphviz to draw the system layout.
origin | destination | link_capacity | weight
well_1 | feed_pump | 1 | 1
well_2 | feed_pump | 1 | 1
commercial_power_supply | feed_pump | 1 | 1
backup_power_supply | feed_pump | 1 | 1
feed_pump | input_pipe_1 | 1 | 1
chem_tank_ph_acid | input_pipe_1 | 1 | 1
chem_tank_coag1 | input_pipe_1 | 1 | 1
input_pipe_1 | pipe_fb_1 | 1 | 1
input_pipe_1 | pipe_fb_2 | 1 | 1
input_pipe_1 | pipe_fb_3 | 1 | 1
input_pipe_1 | pipe_fb_4 | 1 | 1
input_pipe_1 | pipe_fb_5 | 1 | 1
input_pipe_1 | pipe_fb_6 | 1 | 1
input_pipe_1 | pipe_fb_7 | 1 | 1
input_pipe_1 | pipe_fb_8 | 1 | 1
pipe_fb_1 | floc_basin_1 | 1 | 1
pipe_fb_2 | floc_basin_2 | 1 | 1
pipe_fb_3 | floc_basin_3 | 1 | 1
pipe_fb_4 | floc_basin_4 | 1 | 1
pipe_fb_5 | floc_basin_5 | 1 | 1
pipe_fb_6 | floc_basin_6 | 1 | 1
pipe_fb_7 | floc_basin_7 | 1 | 1
pipe_fb_8 | floc_basin_8 | 1 | 1
pump_daf | daf_1 | 1 | 1
pump_daf | daf_2 | 1 | 1
pump_daf | daf_3 | 1 | 1
pump_daf | daf_4 | 1 | 1
pump_daf | daf_5 | 1 | 1
pump_daf | daf_6 | 1 | 1
pump_daf | daf_7 | 1 | 1
pump_daf | daf_8 | 1 | 1
floc_basin_1 | daf_1 | 1 | 1
floc_basin_2 | daf_2 | 1 | 1
floc_basin_3 | daf_3 | 1 | 1
floc_basin_4 | daf_4 | 1 | 1
floc_basin_5 | daf_5 | 1 | 1
floc_basin_6 | daf_6 | 1 | 1
floc_basin_7 | daf_7 | 1 | 1
floc_basin_8 | daf_8 | 1 | 1
daf_1 | connector_daf | 1 | 1
daf_2 | connector_daf | 1 | 1
daf_3 | connector_daf | 1 | 1
daf_4 | connector_daf | 1 | 1
daf_5 | connector_daf | 1 | 1
daf_6 | connector_daf | 1 | 1
daf_7 | connector_daf | 1 | 1
daf_8 | connector_daf | 1 | 1
connector_daf | pipe_oz_1 | 1 | 1
connector_daf | pipe_oz_2 | 1 | 1
pipe_oz_1 | ozone_contact_1 | 1 | 1
pipe_oz_2 | ozone_contact_2 | 1 | 1
ozone_gen | ozone_contact_1 | 1 | 1
ozone_gen | ozone_contact_2 | 1 | 1
ozone_contact_1 | connector_oz | 1 | 1
ozone_contact_2 | connector_oz | 1 | 1
connector_oz | pipe_ft_1 | 1 | 1
connector_oz | pipe_ft_2 | 1 | 1
connector_oz | pipe_ft_3 | 1 | 1
connector_oz | pipe_ft_4 | 1 | 1
connector_oz | pipe_ft_5 | 1 | 1
connector_oz | pipe_ft_6 | 1 | 1
connector_oz | pipe_ft_7 | 1 | 1
connector_oz | pipe_ft_8 | 1 | 1
pipe_ft_1 | filter_tank_1 | 1 | 1
pipe_ft_2 | filter_tank_2 | 1 | 1
pipe_ft_3 | filter_tank_3 | 1 | 1
pipe_ft_4 | filter_tank_4 | 1 | 1
pipe_ft_5 | filter_tank_5 | 1 | 1
pipe_ft_6 | filter_tank_6 | 1 | 1
pipe_ft_7 | filter_tank_7 | 1 | 1
pipe_ft_8 | filter_tank_8 | 1 | 1
filter_tank_1 | pipe_ft_out_1 | 1 | 1
filter_tank_2 | pipe_ft_out_1 | 1 | 1
filter_tank_3 | pipe_ft_out_1 | 1 | 1
filter_tank_4 | pipe_ft_out_1 | 1 | 1
filter_tank_5 | pipe_ft_out_1 | 1 | 1
filter_tank_6 | pipe_ft_out_1 | 1 | 1
filter_tank_7 | pipe_ft_out_1 | 1 | 1
filter_tank_8 | pipe_ft_out_1 | 1 | 1
pipe_ft_out_1 | pipe_ccc_1 | 1 | 1
pipe_ccc_1 | chlorine_contact_chamber | 1 | 1
chlorine_tank | chlorine_contact_chamber | 1 | 1
chem_tank_ph_base | chlorine_contact_chamber | 1 | 1
chlorine_contact_chamber | pipe_to_clearwell | 1 | 1
pipe_to_clearwell | connector_clearwell | 1 | 1
connector_clearwell | clearwell_1 | 1 | 1
connector_clearwell | clearwell_2 | 1 | 1
clearwell_1 | pipe_cw_out_1 | 1 | 1
clearwell_2 | pipe_cw_out_2 | 1 | 1
pipe_cw_out_1 | pipe_connector_cw | 1 | 1
pipe_cw_out_2 | pipe_connector_cw | 1 | 1
pipe_connector_cw | pipe_uv_in_1 | 1 | 1
pipe_connector_cw | pipe_uv_in_2 | 1 | 1
pipe_uv_in_1 | uv_chamber_1 | 1 | 1
pipe_uv_in_1 | uv_chamber_2 | 1 | 1
pipe_uv_in_2 | uv_chamber_3 | 1 | 1
pipe_uv_in_2 | uv_chamber_4 | 1 | 1
pipe_uv_in_2 | uv_chamber_5 | 1 | 1
pipe_uv_in_2 | uv_chamber_6 | 1 | 1
uv_chamber_1 | pipe_connector_uv_out | 1 | 1
uv_chamber_2 | pipe_connector_uv_out | 1 | 1
uv_chamber_3 | pipe_connector_uv_out | 1 | 1
uv_chamber_4 | pipe_connector_uv_out | 1 | 1
uv_chamber_5 | pipe_connector_uv_out | 1 | 1
uv_chamber_6 | pipe_connector_uv_out | 1 | 1
pipe_connector_uv_out | pipe_large_fl_1 | 1 | 1
pipe_connector_uv_out | pipe_large_fl_2 | 1 | 1
chem_tank_Fl | pipe_large_fl_1 | 1 | 1
chem_tank_phosphate | pipe_large_fl_1 | 1 | 1
chem_tank_Fl | pipe_large_fl_2 | 1 | 1
chem_tank_phosphate | pipe_large_fl_2 | 1 | 1
pipe_large_fl_1 | pipe_to_distro_1 | 1 | 1
pipe_large_fl_2 | pipe_to_distro_2 | 1 | 1
pipe_to_distro_1 | output_1 | 1 | 1
pipe_to_distro_2 | output_2 | 1 | 1

## supply_setup
Description: | Necessary input materiél required for plant operation
Note: | Capacity given as percentage
input_node | input_capacity | capacity_fraction | commodity_type
well_1 | 50 | 1 | untreated water
well_2 | 50 | 1 | untreated water
commercial_power_supply | 100 | 1 | electricity

## output_setup
Description: | Treatment Capacity in Mega Litres per Day (MLD)
Note:
output_node | production_node | output_node_capacity | capacity_fraction | priority
output_1 | pipe_to_distro_1 | 200 | 0.5 | 1
output_2 | pipe_to_distro_2 | 200 | 0.5 | 2

## comp_type_dmg_algo
Description: | List of component types with fragility and recovery data
Note: | Fragilities are defined according to discrete damage states. Recovery time is in WEEKS. The suffix SDL refers to component Seismic Design Level. [SDL1: 0.2g PGA, SDL2: 0.35g PGA, SDL3: 0.4g PGA]
component_type | damage_state | damage_function | mode | damage_median | damage_logstd | damage_ratio | functionality | minimum | sigma_1 | sigma_2 | recovery_mean | recovery_std | recovery_95percentile | fragility_source
Electric Power Backup | DS1 Slight | Lognormal | 1 | 0.8 | 0.6 | 0.2 | 0.95 | NA | NA | NA | 0.2 | 0.060796 | 0.1 | NIBS 2003, Table A.8.6, Table 15B.5
Electric Power Backup | DS2 Moderate | Lognormal | 1 | 1 | 0.8 | 0.7 | 0.75 | NA | NA | NA | 0.5 | 0.060796 | 0.1 | NIBS 2003, Table A.8.6, Table 15B.5
Electric Power Backup | DS3 Extensive | Lognormal | 1 | 1.1 | 0.85 | 0.85 | 0.3 | NA | NA | NA | 1 | 0.30398 | 0.5 | NA
Electric Power Backup | DS4 Complete | Lognormal | 1 | 1.4 | 0.8 | 1 | 0 | NA | NA | NA | 4.3 | 0.60796 | 1 | NA
Electric Power Commercial | DS1 Slight | Lognormal | 1 | 0.15 | 0.4 | 0.2 | 0.95 | NA | NA | NA | 3 | 0.60796 | 1 | NIBS 2003, Table A.8.6, Table 15B.5
Electric Power Commercial | DS2 Moderate | Lognormal | 1 | 0.3 | 0.4 | 0.4 | 0.75 | NA | NA | NA | 20 | 1.2159 | 2 | NIBS 2003, Table A.8.6, Table 15B.5
Electric Power Commercial | DS3 Extensive | Lognormal | 1 | 0.8 | 0.4 | 0.75 | 0.3 | NA | NA | NA | 60 | 2.4318 | 4 | NA
Electric Power Commercial | DS4 Complete | Lognormal | 1 | 1.1 | 0.4 | 0.9 | 0 | NA | NA | NA | 102.8571 | 4.8637 | 8 | NA
Sediment Flocculation | DS1 Slight | Lognormal | 1 | 0.36 | 0.5 | 0.2 | 0.95 | NA | NA | NA | 0.2 | 0.060796 | 0.1 | NIBS 2003, Table A.8.6, Table 15B.5
Sediment Flocculation | DS2 Moderate | Lognormal | 1 | 0.6 | 0.5 | 0.5 | 0.75 | NA | NA | NA | 0.5 | 0.060796 | 0.1 | NIBS 2003, Table A.8.6, Table 15B.5
Sediment Flocculation | DS3 Extensive | Lognormal | 1 | 1.2 | 0.6 | 0.8 | 0.3 | NA | NA | NA | 1 | 0.30398 | 0.5 | NIBS 2003, Table B.8.1, Table 15B.6
Sediment Flocculation | DS4 Complete | Lognormal | 1 | 1.5 | 0.6 | 1 | 0 | NA | NA | NA | 4.3 | 0.60796 | 1 | NA
Chlorination Equipment | DS1 Slight | Lognormal | 1 | 0.65 | 0.6 | 0.15 | 0.95 | NA | NA | NA | 1 | 0.30398 | 0.5 | NIBS 2003, Table A.8.6, Table 15B.5
Chlorination Equipment | DS2 Moderate | Lognormal | 1 | 1 | 0.7 | 0.5 | 0.75 | NA | NA | NA | 3 | 0.60796 | 1 | NIBS 2003, Table A.8.6, Table 15B.5
Chlorination Equipment | DS3 Extensive | Lognormal | 1 | 1.15 | 0.6 | 0.8 | 0.3 | NA | NA | NA | 15 | 1.8239 | 3 | NA
Chlorination Equipment | DS4 Complete | Lognormal | 1 | 1.3 | 0.6 | 0.97 | 0 | NA | NA | NA | 30 | 2.4318 | 4 | NA
Pump Station | DS1 Slight | Lognormal | 1 | 0.15 | 0.3 | 0.2 | 0.95 | NA | NA | NA | 5 | 0.18239 | 0.3 | Syner-G D3.5: Table 4-14, Anchored, low-rise RC building, HIGH seismic code
Pump Station | DS2 Moderate | Lognormal | 1 | 0.3 | 0.35 | 0.5 | 0.75 | NA | NA | NA | 10 | 1.2159 | 2 | Syner-G D3.5: Table 4-14, Anchored, low-rise RC building, HIGH seismic code
Pump Station | DS3 Extensive | Lognormal | 1 | 1.1 | 0.55 | 0.8 | 0.3 | NA | NA | NA | 21 | 1.8239 | 3 | Syner-G D3.5: Table 4-14, Anchored, low-rise RC building, HIGH seismic code
Pump Station | DS4 Complete | Lognormal | 1 | 2.1 | 0.7 | 0.95 | 0 | NA | NA | NA | 42.8571 | 2.4318 | 4 | Syner-G D3.5: Table 4-14, Anchored, low-rise RC building, HIGH seismic code
Rectangular Sedimentation Tank | DS1 Slight | Lognormal | 1 | 0.4 | 0.6 | 0.2 | 0.95 | NA | NA | NA | 5 | 0.30398 | 0.5 | ASSUMED: same as 'Basins'
Rectangular Sedimentation Tank | DS2 Moderate | Lognormal | 1 | 0.56 | 0.6 | 0.7 | 0.75 | NA | NA | NA | 17 | 0.60796 | 1 | ASSUMED: same as 'Basins'
Rectangular Sedimentation Tank | DS3 Extensive | Lognormal | 1 | 0.9 | 0.6 | 0.8 | 0.3 | NA | NA | NA | 37 | 1.2159 | 2 | ASSUMED: same as 'Basins'
Rectangular Sedimentation Tank | DS4 Complete | Lognormal | 1 | 1.1 | 0.6 | 0.95 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4 | ASSUMED: same as 'Basins'
Elevated Pipes | DS1 Slight | Lognormal | 1 | 0.25 | 0.6 | 0.2 | 0.95 | NA | NA | NA | 1 | 0.12159 | 0.2 | NA
Elevated Pipes | DS2 Moderate | Lognormal | 1 | 0.36 | 0.6 | 0.5 | 0.75 | NA | NA | NA | 4 | 0.30398 | 0.5 | NA
Elevated Pipes | DS3 Extensive | Lognormal | 1 | 0.53 | 0.6 | 0.65 | 0.3 | NA | NA | NA | 8 | 0.91194 | 1.5 | NIBS 2003, Table A.8.6, Table 15B.5
Elevated Pipes | DS4 Complete | Lognormal | 1 | 1 | 0.6 | 0.9 | 0 | NA | NA | NA | 12 | 1.8239 | 3 | NIBS 2003, Table A.8.6, Table 15B.5
Internal Pipework | DS1 Slight | Lognormal | 1 | 0.25 | 0.6 | 0.2 | 0.95 | NA | NA | NA | 1 | 0.12159 | 0.2 | ASSUMED: same as 'Elevated Pipes'
Internal Pipework | DS2 Moderate | Lognormal | 1 | 0.36 | 0.6 | 0.5 | 0.75 | NA | NA | NA | 4 | 0.30398 | 0.5 | ASSUMED: same as 'Elevated Pipes'
Internal Pipework | DS3 Extensive | Lognormal | 1 | 0.53 | 0.6 | 0.65 | 0.3 | NA | NA | NA | 8 | 0.91194 | 1.5 | ASSUMED: same as 'Elevated Pipes'
Internal Pipework | DS4 Complete | Lognormal | 1 | 1 | 0.6 | 0.9 | 0 | NA | NA | NA | 12 | 1.8239 | 3 | ASSUMED: same as 'Elevated Pipes'
Pipe Connectors | DS1 Slight | Lognormal | 1 | 0.25 | 0.6 | 0.2 | 0.95 | NA | NA | NA | 1 | 0.12159 | 0.2 | ASSUMED: same as 'Elevated Pipes'
Pipe Connectors | DS2 Moderate | Lognormal | 1 | 0.36 | 0.6 | 0.5 | 0.75 | NA | NA | NA | 4 | 0.30398 | 0.5 | ASSUMED: same as 'Elevated Pipes'
Pipe Connectors | DS3 Extensive | Lognormal | 1 | 0.53 | 0.6 | 0.65 | 0.3 | NA | NA | NA | 8 | 0.91194 | 1.5 | ASSUMED: same as 'Elevated Pipes'
Pipe Connectors | DS4 Complete | Lognormal | 1 | 1 | 0.6 | 0.9 | 0 | NA | NA | NA | 12 | 1.8239 | 3 | ASSUMED: same as 'Elevated Pipes'
Basins | DS1 Slight | Lognormal | 1 | 0.4 | 0.6 | 0.2 | 0.95 | NA | NA | NA | 3 | 0.60796 | 1 | NIBS 2003, Table A.8.5
Basins | DS2 Moderate | Lognormal | 1 | 0.67 | 0.7 | 0.7 | 0.75 | NA | NA | NA | 20 | 1.2159 | 2 | NA
Basins | DS3 Extensive | Lognormal | 1 | 0.85 | 0.7 | 0.85 | 0.3 | NA | NA | NA | 60 | 2.4318 | 4 | NA
Basins | DS4 Complete | Lognormal | 1 | 1 | 0.7 | 0.99 | 0 | NA | NA | NA | 102.8571 | 4.8637 | 8 | NA
Chemical Tanks | DS1 Slight | Lognormal | 1 | 0.4 | 0.7 | 0.2 | 0.95 | NA | NA | NA | 5 | 0.30398 | 0.5 | NIBS 2003, Table A.8.6, Table 15B.5
Chemical Tanks | DS2 Moderate | Lognormal | 1 | 0.65 | 0.7 | 0.75 | 0.75 | NA | NA | NA | 17 | 0.60796 | 1 | NIBS 2003, Table A.8.6, Table 15B.5
Chemical Tanks | DS3 Extensive | Lognormal | 1 | 0.95 | 0.7 | 0.85 | 0.3 | NA | NA | NA | 37 | 1.2159 | 2 | NA
Chemical Tanks | DS4 Complete | Lognormal | 1 | 1.18 | 0.7 | 0.9 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4 | NA
Circular Clarification Tank | DS1 Slight | Lognormal | 1 | 0.25 | 0.55 | 0.2 | 0.95 | NA | NA | NA | 5 | 0.30398 | 0.5 | NIBS 2003, Table 8.9 (Algorithm for 'RC Tank - On-Ground - Anchored')
Circular Clarification Tank | DS2 Moderate | Lognormal | 1 | 0.52 | 0.7 | 0.7 | 0.75 | NA | NA | NA | 17 | 0.60796 | 1 | NIBS 2003, Table 8.9 (Algorithm for 'RC Tank - On-Ground - Anchored')
Circular Clarification Tank | DS3 Extensive | Lognormal | 1 | 0.95 | 0.6 | 0.8 | 0.3 | NA | NA | NA | 37 | 1.2159 | 2 | NIBS 2003, Table 8.9 (Algorithm for 'RC Tank - On-Ground - Anchored')
Circular Clarification Tank | DS4 Complete | Lognormal | 1 | 1.64 | 0.7 | 0.99 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4 | NIBS 2003, Table 8.9 (Algorithm for 'RC Tank - On-Ground - Anchored')
Horizontal Pump | DS1 Slight | Lognormal | 1 | 0.53 | 0.63 | 0.2 | 0.95 | NA | NA | NA | 5 | 0.30398 | 0.5 | NA
Horizontal Pump | DS2 Moderate | Lognormal | 1 | 0.92 | 0.65 | 0.45 | 0.75 | NA | NA | NA | 17 | 0.60796 | 1 | NA
Horizontal Pump | DS3 Extensive | Lognormal | 1 | 1.6 | 0.6 | 0.75 | 0.3 | NA | NA | NA | 37 | 1.2159 | 2 | NIBS 2003, Table A.8.1, Table 15B.5
Horizontal Pump | DS4 Complete | Lognormal | 1 | 1.8 | 0.6 | 0.95 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4 | NA
Vertical Pump | DS1 Slight | Lognormal | 1 | 0.6 | 0.6 | 0.2 | 0.95 | NA | NA | NA | 5 | 0.30398 | 0.5 | NA
Vertical Pump | DS2 Moderate | Lognormal | 1 | 0.85 | 0.6 | 0.45 | 0.75 | NA | NA | NA | 17 | 0.60796 | 1 | NA
Vertical Pump | DS3 Extensive | Lognormal | 1 | 1.25 | 0.6 | 0.75 | 0.3 | NA | NA | NA | 37 | 1.2159 | 2 | NIBS 2003, Table A.8.1, Table 15B.5
Vertical Pump | DS4 Complete | Lognormal | 1 | 1.5 | 0.6 | 0.95 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4 | NA
Buildings | DS1 Slight | Lognormal | 1 | 0.28 | 0.73 | 0.1 | 0.95 | NA | NA | NA | 5 | 0.60796 | 1 | NIBS 2003, Table A.8.1, Table 15B.5
Buildings | DS2 Moderate | Lognormal | 1 | 0.72 | 0.73 | 0.4 | 0.75 | NA | NA | NA | 20 | 1.2159 | 2 | NIBS 2003, Table A.8.1, Table 15B.5
Buildings | DS3 Extensive | Lognormal | 1 | 1.66 | 0.73 | 0.8 | 0.3 | NA | NA | NA | 50 | 2.4318 | 4 | NIBS 2003, Table A.8.1, Table 15B.5
Buildings | DS4 Complete | Lognormal | 1 | 2.17 | 0.73 | 1 | 0 | NA | NA | NA | 102.8571 | 4.8637 | 8 | NIBS 2003, Table A.8.1, Table 15B.5
Wells | DS1 Slight | Lognormal | 1 | 0.15 | 0.75 | 0.2 | 0.95 | NA | NA | NA | 5 | 0.30398 | 0.5 | NIBS 2003, Table 8.8
Wells | DS2 Moderate | Lognormal | 1 | 0.36 | 0.65 | 0.45 | 0.75 | NA | NA | NA | 17 | 0.60796 | 1 | NIBS 2003, Table 8.8
Wells | DS3 Extensive | Lognormal | 1 | 0.72 | 0.65 | 0.75 | 0.3 | NA | NA | NA | 37 | 1.2159 | 2 | NIBS 2003, Table 8.8
Wells | DS4 Complete | Lognormal | 1 | 1.5 | 0.8 | 0.95 | 0 | NA | NA | NA | 77.1429 | 2.4318 | 4 | NIBS 2003, Table 8.8
SYSTEM_OUTPUT | DS1 Slight | Lognormal | 1 | 10 | 1 | 0 | 1 | NA | NA | NA | 5 | 0.30398 | 0.5 | Unbreakable - Model Artifact
SYSTEM_OUTPUT | DS2 Moderate | Lognormal | 1 | 10 | 1 | 0 | 1 | NA | NA | NA | 17 | 0.60796 | 1 | Unbreakable - Model Artifact
SYSTEM_OUTPUT | DS3 Extensive | Lognormal | 1 | 10 | 1 | 0 | 1 | NA | NA | NA | 37 | 1.2159 | 2 | Unbreakable - Model Artifact
SYSTEM_OUTPUT | DS4 Complete | Lognormal | 1 | 10 | 1 | 0 | 1 | NA | NA | NA | 77.1429 | 2.4318 | 4 | Unbreakable - Model Artifact

## damage_state_def
Description: | Definitions of damage states of the list of component types in the system
Note:
component_type | damage_state | damage_state_definition
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete
DS1 Slight
DS2 Moderate
DS3 Extensive
DS4 Complete

## asset_names
Component Types | Synonyms
Baffles
Basins
Buildings
Chemical Tanks
Chlorination Equipment
Circular Clarification Tank
Electric Power Backup
Electric Power Commercial
Elevated Pipes
Flow Equalisation Basin
Grit Chamber
Horizontal Pump
Paddles
Power Station Gas Fired
Primary Clarifier Tank
Pump Station
Rectangular Sedimentation Tank
Reservoir
Scrapers
Secondary Treatment Tank
Sediment Flocculation
Sludge Digesters
Step Screens
Vertical Pump
Voltage Transformer
Wells
Internal Pipework
Pipe Connectors
SYSTEM_OUTPUT

## comps_to_add
pipe_to_processing