## table_description
table | description | note
component_list | This file lists the instances of various component types within the system. Component design level x.xx g. | Cost fractions define economic value of the individual component relative to the cost of entire system.
component_connections | Network connections. Each pair of nodes implies a connecting edge. Directionality is defined by order of nodes in a row (Orig -> Dest). | Used by: (1) network algorithm package for flow calculations, (2) Pygraphviz to draw the system layout.
supply_setup | Necessary input materiél required for plant operation | Capacity given as percentage
output_setup | Treatment Capacity in Mega Litres per Day (MLD)
comp_type_dmg_algo | List of component types with fragility and recovery data | Fragilities are defined according to discrete damage states. Recovery time is in WEEKS. The suffix SDL refers to component Seismic Design Level. [SDL1: 0.2g PGA, SDL2: 0.35g PGA, SDL3: 0.4g PGA]
damage_state_def | Definitions of damage states of the list of component types in the system

## component_list
component_id | component_type | component_class | cost_fraction | node_type | node_cluster | op_capacity
commercial_power_supply | Electric Power Commercial | Energy Source | 0.02 | supply | Supply | 1
backup_power_supply | Electric Power Backup | Energy Source | 0.04 | supply | Supply | 1
well_1 | Wells | Water Supply | 0.041 | supply | Supply | 1
well_2 | Wells | Water Supply | 0.041 | supply | Supply | 1
feed_pump | Vertical Pump | Water Supply | 0.0025 | transshipment | Supply | 1
input_pipe_1 | Internal Pipework | Water Supply Pipe | 0.0025 | transshipment | Supply | 1
chem_tank_ph_acid | Chemical Tanks | Chem Dosage Stage 1 | 0.033 | dependency | none | 1
chem_tank_coag1 | Chemical Tanks | Chem Dosage Stage 1 | 0.033 | dependency | none | 1
pipe_fb_1 | Internal Pipework | Coagulation and Flocculation Inlets | 0.0025 | transshipment | Coagulation and Flocculation Inlets | 1
pipe_fb_2 | Internal Pipework | Coagulation and Flocculation Inlets | 0.0025 | transshipment | Coagulation and Flocculation Inlets | 1
pipe_fb_3 | Internal Pipework | Coagulation and Flocculation Inlets | 0.0025 | transshipment | Coagulation and Flocculation Inlets | 1
pipe_fb_4 | Internal Pipework | Coagulation and Flocculation Inlets | 0.0025 | transshipment | Coagulation and Flocculation Inlets | 1
pipe_fb_5 | Internal Pipework | Coagulation and Flocculation Inlets | 0.0025 | transshipment | Coagulation and Flocculation Inlets | 1
pipe_fb_6 | Internal Pipework | Coagulation and Flocculation Inlets | 0.0025 | transshipment | Coagulation and Flocculation Inlets | 1
pipe_fb_7 | Internal Pipework | Coagulation and Flocculation Inlets | 0.0025 | transshipment | Coagulation and Flocculation Inlets | 1
pipe_fb_8 | Internal Pipework | Coagulation and Flocculation Inlets | 0.0025 | transshipment | Coagulation and Flocculation Inlets | 1
floc_basin_1 | Sediment Flocculation | Coagulation and Flocculation | 0.0075 | transshipment | Coagulation and Flocculation | 1
floc_basin_2 | Sediment Flocculation | Coagulation and Flocculation | 0.0075 | transshipment | Coagulation and Flocculation | 1
floc_basin_3 | Sediment Flocculation | Coagulation and Flocculation | 0.0075 | transshipment | Coagulation and Flocculation | 1
floc_basin_4 | Sediment Flocculation | Coagulation and Flocculation | 0.0075 | transshipment | Coagulation and Flocculation | 1
floc_basin_5 | Sediment Flocculation | Coagulation and Flocculation | 0.0075 | transshipment | Coagulation and Flocculation | 1
floc_basin_6 | Sediment Flocculation | Coagulation and Flocculation | 0.0075 | transshipment | Coagulation and Flocculation | 1
floc_basin_7 | Sediment Flocculation | Coagulation and Flocculation | 0.0075 | transshipment | Coagulation and Flocculation | 1
floc_basin_8 | Sediment Flocculation | Coagulation and Flocculation | 0.0075 | transshipment | Coagulation and Flocculation | 1
pump_daf | Horizontal Pump | DAF Connector and Pump | 0.005 | dependency | none | 1
daf_1 | Basins | Dissolved Air Flotation | 0.0075 | transshipment | Dissolved Air Flotation | 1
daf_2 | Basins | Dissolved Air Flotation | 0.0075 | transshipment | Dissolved Air Flotation | 1
daf_3 | Basins | Dissolved Air Flotation | 0.0075 | transshipment | Dissolved Air Flotation | 1
daf_4 | Basins | Dissolved Air Flotation | 0.0075 | transshipment | Dissolved Air Flotation | 1
daf_5 | Basins | Dissolved Air Flotation | 0.0075 | transshipment | Dissolved Air Flotation | 1
daf_6 | Basins | Dissolved Air Flotation | 0.0075 | transshipment | Dissolved Air Flotation | 1
daf_7 | Basins | Dissolved Air Flotation | 0.0075 | transshipment | Dissolved Air Flotation | 1
daf_8 | Basins | Dissolved Air Flotation | 0.0075 | transshipment | Dissolved Air Flotation | 1
connector_daf | Pipe Connectors | DAF Connector and Pump | 0.0025 | transshipment | DAF Connector | 1
pipe_oz_1 | Internal Pipework | Ozone Disinfection Pipework | 0.0025 | transshipment | Ozone Disinfection Pipework | 1
pipe_oz_2 | Internal Pipework | Ozone Disinfection Pipework | 0.0025 | transshipment | Ozone Disinfection Pipework | 1
ozone_gen | Chemical Tanks | Ozone Disinfection | 0.0025 | dependency | Ozone Disinfection | 1
ozone_contact_1 | Basins | Ozone Disinfection | 0.025 | transshipment | Ozone Disinfection | 1
ozone_contact_2 | Basins | Ozone Disinfection | 0.025 | transshipment | Ozone Disinfection | 1
connector_oz | Pipe Connectors | Ozone Disinfection Connector | 0.0025 | transshipment | Ozone Disinfection Connector | 1
pipe_ft_1 | Internal Pipework | Filtration Inlet Pipework | 0.0025 | transshipment | Filtration Inlet Pipework | 1
pipe_ft_2 | Internal Pipework | Filtration Inlet Pipework | 0.0025 | transshipment | Filtration Inlet Pipework | 1
pipe_ft_3 | Internal Pipework | Filtration Inlet Pipework | 0.0025 | transshipment | Filtration Inlet Pipework | 1
pipe_ft_4 | Internal Pipework | Filtration Inlet Pipework | 0.0025 | transshipment | Filtration Inlet Pipework | 1
pipe_ft_5 | Internal Pipework | Filtration Inlet Pipework | 0.0025 | transshipment | Filtration Inlet Pipework | 1
pipe_ft_6 | Internal Pipework | Filtration Inlet Pipework | 0.0025 | transshipment | Filtration Inlet Pipework | 1
pipe_ft_7 | Internal Pipework | Filtration Inlet Pipework | 0.0025 | transshipment | Filtration Inlet Pipework | 1
pipe_ft_8 | Internal Pipework | Filtration Inlet Pipework | 0.0025 | transshipment | Filtration Inlet Pipework | 1
filter_tank_1 | Basins | Filtration Tanks | 0.025 | transshipment | Filtration Tanks | 1
filter_tank_2 | Basins | Filtration Tanks | 0.025 | transshipment | Filtration Tanks | 1
filter_tank_3 | Basins | Filtration Tanks | 0.025 | transshipment | Filtration Tanks | 1
filter_tank_4 | Basins | Filtration Tanks | 0.025 | transshipment | Filtration Tanks | 1
filter_tank_5 | Basins | Filtration Tanks | 0.025 | transshipment | Filtration Tanks | 1
filter_tank_6 | Basins | Filtration Tanks | 0.025 | transshipment | Filtration Tanks | 1
filter_tank_7 | Basins | Filtration Tanks | 0.025 | transshipment | Filtration Tanks | 1
filter_tank_8 | Basins | Filtration Tanks | 0.025 | transshipment | Filtration Tanks | 1
pipe_ft_out_1 | Internal Pipework | Filtration Output Pipework | 0.0025 | transshipment | Filtration Ouput Pipework | 1
pipe_ccc_1 | Internal Pipework | Chlorine Disinfection Pipework | 0.0025 | transshipment | Chlorine Disinfection Pipework | 1
chlorine_tank | Chemical Tanks | Chlorine Disinfection | 0.033 | dependency | Chlorine Disinfection | 1
chem_tank_ph_base | Chemical Tanks | Chlorine Disinfection | 0.033 | dependency | Chlorine Disinfection | 1
chlorine_contact_chamber | Basins | Chlorine Disinfection | 0.0025 | transshipment | Chlorine Disinfection | 1
pipe_to_clearwell | Internal Pipework | Settling | 0.0025 | transshipment | Clearwell Input Pipework | 1
connector_clearwell | Pipe Connectors | Settling | 0.0025 | transshipment | Clearwell Input Connector | 1
clearwell_1 | Basins | Reservoir | 0.0025 | transshipment | Clearwell | 1
clearwell_2 | Basins | Reservoir | 0.0025 | transshipment | Clearwell | 1
pipe_cw_out_1 | Internal Pipework | Reticulation | 0.0025 | transshipment | Clearwell Output Pipe | 1
pipe_cw_out_2 | Internal Pipework | Reticulation | 0.0025 | transshipment | Clearwell Output Pipe | 1
pipe_connector_cw | Pipe Connectors | Reticulation | 0.0025 | transshipment | Clearwell Output Connector | 1
pipe_uv_in_1 | Internal Pipework | UV Disinfection Input | 0.0025 | transshipment | UV Disinfection Input | 1
pipe_uv_in_2 | Internal Pipework | UV Disinfection Input | 0.0025 | transshipment | UV Disinfection Input | 1
uv_chamber_1 | Basins | UV Disinfection | 0.025 | transshipment | UV Disinfection | 1
uv_chamber_2 | Basins | UV Disinfection | 0.025 | transshipment | UV Disinfection | 1
uv_chamber_3 | Basins | UV Disinfection | 0.025 | transshipment | UV Disinfection | 1
uv_chamber_4 | Basins | UV Disinfection | 0.025 | transshipment | UV Disinfection | 1
uv_chamber_5 | Basins | UV Disinfection | 0.025 | transshipment | UV Disinfection | 1
uv_chamber_6 | Basins | UV Disinfection | 0.025 | transshipment | UV Disinfection | 1
pipe_connector_uv_out | Pipe Connectors | UV Disinfection Output | 0.0025 | transshipment | UV Disinfection Output | 1
pipe_large_fl_1 | Internal Pipework | Water Conditioning | 0.0035 | transshipment | Water Conditioning | 1
pipe_large_fl_2 | Internal Pipework | Water Conditioning | 0.0035 | transshipment | Water Conditioning | 1
chem_tank_Fl | Chemical Tanks | Water Conditioning | 0.033 | dependency | none | 1
chem_tank_phosphate | Chemical Tanks | Water Conditioning | 0.033 | dependency | none | 1
pipe_to_distro_1 | Elevated Pipes | Supply to Distribution | 0.004 | transshipment | Supply to Distribution | 1
pipe_to_distro_2 | Elevated Pipes | Supply to Distribution | 0.004 | transshipment | Supply to Distribution | 1
output_1 | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | OUTPUT | 1
output_2 | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | OUTPUT | 1

## component_connections
origin | destination | link_capacity | weight
well_1 | feed_pump | 1 | 1
well_2 | feed_pump | 1 | 1
commercial_power_supply | feed_pump | 1 | 1
backup_power_supply | feed_pump | 1 | 1
feed_pump | input_pipe_1 | 1 | 1
chem_tank_ph_acid | input_pipe_1 | 1 | 1
chem_tank_coag1 | input_pipe_1 | 1 | 1
input_pipe_1 | pipe_fb_1 | 1 | 1
input_pipe_1 | pipe_fb_2 | 1 | 1
input_pipe_1 | pipe_fb_3 | 1 | 1
input_pipe_1 | pipe_fb_4 | 1 | 1
input_pipe_1 | pipe_fb_5 | 1 | 1
input_pipe_1 | pipe_fb_6 | 1 | 1
input_pipe_1 | pipe_fb_7 | 1 | 1
input_pipe_1 | pipe_fb_8 | 1 | 1
pipe_fb_1 | floc_basin_1 | 1 | 1
pipe_fb_2 | floc_basin_2 | 1 | 1
pipe_fb_3 | floc_basin_3 | 1 | 1
pipe_fb_4 | floc_basin_4 | 1 | 1
pipe_fb_5 | floc_basin_5 | 1 | 1
pipe_fb_6 | floc_basin_6 | 1 | 1
pipe_fb_7 | floc_basin_7 | 1 | 1
pipe_fb_8 | floc_basin_8 | 1 | 1
pump_daf | daf_1 | 1 | 1
pump_daf | daf_2 | 1 | 1
pump_daf | daf_3 | 1 | 1
pump_daf | daf_4 | 1 | 1
pump_daf | daf_5 | 1 | 1
pump_daf | daf_6 | 1 | 1
pump_daf | daf_7 | 1 | 1
pump_daf | daf_8 | 1 | 1
floc_basin_1 | daf_1 | 1 | 1
floc_basin_2 | daf_2 | 1 | 1
floc_basin_3 | daf_3 | 1 | 1
floc_basin_4 | daf_4 | 1 | 1
floc_basin_5 | daf_5 | 1 | 1
floc_basin_6 | daf_6 | 1 | 1
floc_basin_7 | daf_7 | 1 | 1
floc_basin_8 | daf_8 | 1 | 1
daf_1 | connector_daf | 1 | 1
daf_2 | connector_daf | 1 | 1
daf_3 | connector_daf | 1 | 1
daf_4 | connector_daf | 1 | 1
daf_5 | connector_daf | 1 | 1
daf_6 | connector_daf | 1 | 1
daf_7 | connector_daf | 1 | 1
daf_8 | connector_daf | 1 | 1
connector_daf | pipe_oz_1 | 1 | 1
connector_daf | pipe_oz_2 | 1 | 1
pipe_oz_1 | ozone_contact_1 | 1 | 1
pipe_oz_2 | ozone_contact_2 | 1 | 1
ozone_gen | ozone_contact_1 | 1 | 1
ozone_gen | ozone_contact_2 | 1 | 1
ozone_contact_1 | connector_oz | 1 | 1
ozone_contact_2 | connector_oz | 1 | 1
connector_oz | pipe_ft_1 | 1 | 1
connector_oz | pipe_ft_2 | 1 | 1
connector_oz | pipe_ft_3 | 1 | 1
connector_oz | pipe_ft_4 | 1 | 1
connector_oz | pipe_ft_5 | 1 | 1
connector_oz | pipe_ft_6 | 1 | 1
connector_oz | pipe_ft_7 | 1 | 1
connector_oz | pipe_ft_8 | 1 | 1
pipe_ft_1 | filter_tank_1 | 1 | 1
pipe_ft_2 | filter_tank_2 | 1 | 1
pipe_ft_3 | filter_tank_3 | 1 | 1
pipe_ft_4 | filter_tank_4 | 1 | 1
pipe_ft_5 | filter_tank_5 | 1 | 1
pipe_ft_6 | filter_tank_6 | 1 | 1
pipe_ft_7 | filter_tank_7 | 1 | 1
pipe_ft_8 | filter_tank_8 | 1 | 1
filter_tank_1 | pipe_ft_out_1 | 1 | 1
filter_tank_2 | pipe_ft_out_1 | 1 | 1
filter_tank_3 | pipe_ft_out_1 | 1 | 1
filter_tank_4 | pipe_ft_out_1 | 1 | 1
filter_tank_5 | pipe_ft_out_1 | 1 | 1
filter_tank_6 | pipe_ft_out_1 | 1 | 1
filter_tank_7 | pipe_ft_out_1 | 1 | 1
filter_tank_8 | pipe_ft_out_1 | 1 | 1
pipe_ft_out_1 | pipe_ccc_1 | 1 | 1
pipe_ccc_1 | chlorine_contact_chamber | 1 | 1
chlorine_tank | chlorine_contact_chamber | 1 | 1
chem_tank_ph_base | chlorine_contact_chamber | 1 | 1
chlorine_contact_chamber | pipe_to_clearwell | 1 | 1
pipe_to_clearwell | connector_clearwell | 1 | 1
connector_clearwell | clearwell_1 | 1 | 1
connector_clearwell | clearwell_2 | 1 | 1
clearwell_1 | pipe_cw_out_1 | 1 | 1
clearwell_2 | pipe_cw_out_2 | 1 | 1
pipe_cw_out_1 | pipe_connector_cw | 1 | 1
pipe_cw_out_2 | pipe_connector_cw | 1 | 1
pipe_connector_cw | pipe_uv_in_1 | 1 | 1
pipe_connector_cw | pipe_uv_in_2 | 1 | 1
pipe_uv_in_1 | uv_chamber_1 | 1 | 1
pipe_uv_in_1 | uv_chamber_2 | 1 | 1
pipe_uv_in_2 | uv_chamber_3 | 1 | 1
pipe_uv_in_2 | uv_chamber_4 | 1 | 1
pipe_uv_in_2 | uv_chamber_5 | 1 | 1
pipe_uv_in_2 | uv_chamber_6 | 1 | 1
uv_chamber_1 | pipe_connector_uv_out | 1 | 1
uv_chamber_2 | pipe_connector_uv_out | 1 | 1
uv_chamber_3 | pipe_connector_uv_out | 1 | 1
uv_chamber_4 | pipe_connector_uv_out | 1 | 1
uv_chamber_5 | pipe_connector_uv_out | 1 | 1
uv_chamber_6 | pipe_connector_uv_out | 1 | 1
pipe_connector_uv_out | pipe_large_fl_1 | 1 | 1
pipe_connector_uv_out | pipe_large_fl_2 | 1 | 1
chem_tank_Fl | pipe_large_fl_1 | 1 | 1
chem_tank_phosphate | pipe_large_fl_1 | 1 | 1
chem_tank_Fl | pipe_large_fl_2 | 1 | 1
chem_tank_phosphate | pipe_large_fl_2 | 1 | 1
pipe_large_fl_1 | pipe_to_distro_1 | 1 | 1
pipe_large_fl_2 | pipe_to_distro_2 | 1 | 1
pipe_to_distro_1 | output_1 | 1 | 1
pipe_to_distro_2 | output_2 | 1 | 1

## supply_setup
input_node | input_capacity | capacity_fraction | commodity_type
well_1 | 50 | 1 | untreated water
well_2 | 50 | 1 | untreated water
commercial_power_supply | 100 | 1 | electricity

## output_setup
output_node | production_node | output_node_capacity | capacity_fraction | priority
output_1 | pipe_to_distro_1 | 200 | 0.5 | 1
output_2 | pipe_to_distro_2 | 200 | 0.5 | 2

## comp_type_dmg_algo
id | component_type | damage_state | is_piecewise | damage_function | median | location | beta | damage_ratio | functionality | minimum | upper_limit | lower_limit | recovery_function | recovery_function | recovery_mean | recovery_std | recovery_95percentile | fragility_source
1 | Electric Power Backup | DS1 Slight | no | Lognormal | 0.8 | 0 | 0.6 | 0.2 | 0.95 | NA | null | null | Normal | Normal | 0.2 | 0.060796 | 0.1 | NIBS 2003, Table A.8.6, Table 15B.5
2 | Electric Power Backup | DS2 Moderate | no | Lognormal | 1 | 0 | 0.8 | 0.7 | 0.75 | NA | null | null | Normal | Normal | 0.5 | 0.060796 | 0.1 | NIBS 2003, Table A.8.6, Table 15B.5
3 | Electric Power Backup | DS3 Extensive | no | Lognormal | 1.1 | 0 | 0.85 | 0.85 | 0.3 | NA | null | null | Normal | Normal | 1 | 0.30398 | 0.5 | Not Available.
4 | Electric Power Backup | DS4 Complete | no | Lognormal | 1.4 | 0 | 0.8 | 1 | 0 | NA | null | null | Normal | Normal | 4.3 | 0.60796 | 1 | Not Available.
5 | Electric Power Commercial | DS1 Slight | no | Lognormal | 0.15 | 0 | 0.4 | 0.2 | 0.95 | NA | null | null | Normal | Normal | 3 | 0.60796 | 1 | NIBS 2003, Table A.8.6, Table 15B.5
6 | Electric Power Commercial | DS2 Moderate | no | Lognormal | 0.3 | 0 | 0.4 | 0.4 | 0.75 | NA | null | null | Normal | Normal | 20 | 1.2159 | 2 | NIBS 2003, Table A.8.6, Table 15B.5
7 | Electric Power Commercial | DS3 Extensive | no | Lognormal | 0.8 | 0 | 0.4 | 0.75 | 0.3 | NA | null | null | Normal | Normal | 60 | 2.4318 | 4 | Not Available.
8 | Electric Power Commercial | DS4 Complete | no | Lognormal | 1.1 | 0 | 0.4 | 0.9 | 0 | NA | null | null | Normal | Normal | 102.8571 | 4.8637 | 8 | Not Available.
9 | Sediment Flocculation | DS1 Slight | no | Lognormal | 0.36 | 0 | 0.5 | 0.2 | 0.95 | NA | null | null | Normal | Normal | 0.2 | 0.060796 | 0.1 | NIBS 2003, Table A.8.6, Table 15B.5
10 | Sediment Flocculation | DS2 Moderate | no | Lognormal | 0.6 | 0 | 0.5 | 0.5 | 0.75 | NA | null | null | Normal | Normal | 0.5 | 0.060796 | 0.1 | NIBS 2003, Table A.8.6, Table 15B.5
11 | Sediment Flocculation | DS3 Extensive | no | Lognormal | 1.2 | 0 | 0.6 | 0.8 | 0.3 | NA | null | null | Normal | Normal | 1 | 0.30398 | 0.5 | NIBS 2003, Table B.8.1, Table 15B.6
12 | Sediment Flocculation | DS4 Complete | no | Lognormal | 1.5 | 0 | 0.6 | 1 | 0 | NA | null | null | Normal | Normal | 4.3 | 0.60796 | 1 | Not Available.
13 | Chlorination Equipment | DS1 Slight | no | Lognormal | 0.65 | 0 | 0.6 | 0.15 | 0.95 | NA | null | null | Normal | Normal | 1 | 0.30398 | 0.5 | NIBS 2003, Table A.8.6, Table 15B.5
14 | Chlorination Equipment | DS2 Moderate | no | Lognormal | 1 | 0 | 0.7 | 0.5 | 0.75 | NA | null | null | Normal | Normal | 3 | 0.60796 | 1 | NIBS 2003, Table A.8.6, Table 15B.5
15 | Chlorination Equipment | DS3 Extensive | no | Lognormal | 1.15 | 0 | 0.6 | 0.8 | 0.3 | NA | null | null | Normal | Normal | 15 | 1.8239 | 3 | Not Available.
16 | Chlorination Equipment | DS4 Complete | no | Lognormal | 1.3 | 0 | 0.6 | 0.97 | 0 | NA | null | null | Normal | Normal | 30 | 2.4318 | 4 | Not Available.
17 | Pump Station | DS1 Slight | no | Lognormal | 0.15 | 0 | 0.3 | 0.2 | 0.95 | NA | null | null | Normal | Normal | 5 | 0.18239 | 0.3 | Syner-G D3.5: Table 4-14, Anchored, low-rise RC building, HIGH seismic code
18 | Pump Station | DS2 Moderate | no | Lognormal | 0.3 | 0 | 0.35 | 0.5 | 0.75 | NA | null | null | Normal | Normal | 10 | 1.2159 | 2 | Syner-G D3.5: Table 4-14, Anchored, low-rise RC building, HIGH seismic code
19 | Pump Station | DS3 Extensive | no | Lognormal | 1.1 | 0 | 0.55 | 0.8 | 0.3 | NA | null | null | Normal | Normal | 21 | 1.8239 | 3 | Syner-G D3.5: Table 4-14, Anchored, low-rise RC building, HIGH seismic code
20 | Pump Station | DS4 Complete | no | Lognormal | 2.1 | 0 | 0.7 | 0.95 | 0 | NA | null | null | Normal | Normal | 42.8571 | 2.4318 | 4 | Syner-G D3.5: Table 4-14, Anchored, low-rise RC building, HIGH seismic code
21 | Rectangular Sedimentation Tank | DS1 Slight | no | Lognormal | 0.4 | 0 | 0.6 | 0.2 | 0.95 | NA | null | null | Normal | Normal | 5 | 0.30398 | 0.5 | ASSUMED: same as 'Basins'
22 | Rectangular Sedimentation Tank | DS2 Moderate | no | Lognormal | 0.56 | 0 | 0.6 | 0.7 | 0.75 | NA | null | null | Normal | Normal | 17 | 0.60796 | 1 | ASSUMED: same as 'Basins'
23 | Rectangular Sedimentation Tank | DS3 Extensive | no | Lognormal | 0.9 | 0 | 0.6 | 0.8 | 0.3 | NA | null | null | Normal | Normal | 37 | 1.2159 | 2 | ASSUMED: same as 'Basins'
24 | Rectangular Sedimentation Tank | DS4 Complete | no | Lognormal | 1.1 | 0 | 0.6 | 0.95 | 0 | NA | null | null | Normal | Normal | 77.1429 | 2.4318 | 4 | ASSUMED: same as 'Basins'
25 | Elevated Pipes | DS1 Slight | no | Lognormal | 0.25 | 0 | 0.6 | 0.2 | 0.95 | NA | null | null | Normal | Normal | 1 | 0.12159 | 0.2 | Not Available.
26 | Elevated Pipes | DS2 Moderate | no | Lognormal | 0.36 | 0 | 0.6 | 0.5 | 0.75 | NA | null | null | Normal | Normal | 4 | 0.30398 | 0.5 | Not Available.
27 | Elevated Pipes | DS3 Extensive | no | Lognormal | 0.53 | 0 | 0.6 | 0.65 | 0.3 | NA | null | null | Normal | Normal | 8 | 0.91194 | 1.5 | NIBS 2003, Table A.8.6, Table 15B.5
28 | Elevated Pipes | DS4 Complete | no | Lognormal | 1 | 0 | 0.6 | 0.9 | 0 | NA | null | null | Normal | Normal | 12 | 1.8239 | 3 | NIBS 2003, Table A.8.6, Table 15B.5
29 | Internal Pipework | DS1 Slight | no | Lognormal | 0.25 | 0 | 0.6 | 0.2 | 0.95 | NA | null | null | Normal | Normal | 1 | 0.12159 | 0.2 | ASSUMED: same as 'Elevated Pipes'
30 | Internal Pipework | DS2 Moderate | no | Lognormal | 0.36 | 0 | 0.6 | 0.5 | 0.75 | NA | null | null | Normal | Normal | 4 | 0.30398 | 0.5 | ASSUMED: same as 'Elevated Pipes'
31 | Internal Pipework | DS3 Extensive | no | Lognormal | 0.53 | 0 | 0.6 | 0.65 | 0.3 | NA | null | null | Normal | Normal | 8 | 0.91194 | 1.5 | ASSUMED: same as 'Elevated Pipes'
32 | Internal Pipework | DS4 Complete | no | Lognormal | 1 | 0 | 0.6 | 0.9 | 0 | NA | null | null | Normal | Normal | 12 | 1.8239 | 3 | ASSUMED: same as 'Elevated Pipes'
33 | Pipe Connectors | DS1 Slight | no | Lognormal | 0.25 | 0 | 0.6 | 0.2 | 0.95 | NA | null | null | Normal | Normal | 1 | 0.12159 | 0.2 | ASSUMED: same as 'Elevated Pipes'
34 | Pipe Connectors | DS2 Moderate | no | Lognormal | 0.36 | 0 | 0.6 | 0.5 | 0.75 | NA | null | null | Normal | Normal | 4 | 0.30398 | 0.5 | ASSUMED: same as 'Elevated Pipes'
35 | Pipe Connectors | DS3 Extensive | no | Lognormal | 0.53 | 0 | 0.6 | 0.65 | 0.3 | NA | null | null | Normal | Normal | 8 | 0.91194 | 1.5 | ASSUMED: same as 'Elevated Pipes'
36 | Pipe Connectors | DS4 Complete | no | Lognormal | 1 | 0 | 0.6 | 0.9 | 0 | NA | null | null | Normal | Normal | 12 | 1.8239 | 3 | ASSUMED: same as 'Elevated Pipes'
37 | Basins | DS1 Slight | no | Lognormal | 0.4 | 0 | 0.6 | 0.2 | 0.95 | NA | null | null | Normal | Normal | 3 | 0.60796 | 1 | NIBS 2003, Table A.8.5
38 | Basins | DS2 Moderate | no | Lognormal | 0.67 | 0 | 0.7 | 0.7 | 0.75 | NA | null | null | Normal | Normal | 20 | 1.2159 | 2 | Not Available.
39 | Basins | DS3 Extensive | no | Lognormal | 0.85 | 0 | 0.7 | 0.85 | 0.3 | NA | null | null | Normal | Normal | 60 | 2.4318 | 4 | Not Available.
40 | Basins | DS4 Complete | no | Lognormal | 1 | 0 | 0.7 | 0.99 | 0 | NA | null | null | Normal | Normal | 102.8571 | 4.8637 | 8 | Not Available.
41 | Chemical Tanks | DS1 Slight | no | Lognormal | 0.4 | 0 | 0.7 | 0.2 | 0.95 | NA | null | null | Normal | Normal | 5 | 0.30398 | 0.5 | NIBS 2003, Table A.8.6, Table 15B.5
42 | Chemical Tanks | DS2 Moderate | no | Lognormal | 0.65 | 0 | 0.7 | 0.75 | 0.75 | NA | null | null | Normal | Normal | 17 | 0.60796 | 1 | NIBS 2003, Table A.8.6, Table 15B.5
43 | Chemical Tanks | DS3 Extensive | no | Lognormal | 0.95 | 0 | 0.7 | 0.85 | 0.3 | NA | null | null | Normal | Normal | 37 | 1.2159 | 2 | Not Available.
44 | Chemical Tanks | DS4 Complete | no | Lognormal | 1.18 | 0 | 0.7 | 0.9 | 0 | NA | null | null | Normal | Normal | 77.1429 | 2.4318 | 4 | Not Available.
45 | Circular Clarification Tank | DS1 Slight | no | Lognormal | 0.25 | 0 | 0.55 | 0.2 | 0.95 | NA | null | null | Normal | Normal | 5 | 0.30398 | 0.5 | NIBS 2003, Table 8.9 (Algorithm for 'RC Tank - On-Ground - Anchored')
46 | Circular Clarification Tank | DS2 Moderate | no | Lognormal | 0.52 | 0 | 0.7 | 0.7 | 0.75 | NA | null | null | Normal | Normal | 17 | 0.60796 | 1 | NIBS 2003, Table 8.9 (Algorithm for 'RC Tank - On-Ground - Anchored')
47 | Circular Clarification Tank | DS3 Extensive | no | Lognormal | 0.95 | 0 | 0.6 | 0.8 | 0.3 | NA | null | null | Normal | Normal | 37 | 1.2159 | 2 | NIBS 2003, Table 8.9 (Algorithm for 'RC Tank - On-Ground - Anchored')
48 | Circular Clarification Tank | DS4 Complete | no | Lognormal | 1.64 | 0 | 0.7 | 0.99 | 0 | NA | null | null | Normal | Normal | 77.1429 | 2.4318 | 4 | NIBS 2003, Table 8.9 (Algorithm for 'RC Tank - On-Ground - Anchored')
49 | Horizontal Pump | DS1 Slight | no | Lognormal | 0.53 | 0 | 0.63 | 0.2 | 0.95 | NA | null | null | Normal | Normal | 5 | 0.30398 | 0.5 | Not Available.
50 | Horizontal Pump | DS2 Moderate | no | Lognormal | 0.92 | 0 | 0.65 | 0.45 | 0.75 | NA | null | null | Normal | Normal | 17 | 0.60796 | 1 | Not Available.
51 | Horizontal Pump | DS3 Extensive | no | Lognormal | 1.6 | 0 | 0.6 | 0.75 | 0.3 | NA | null | null | Normal | Normal | 37 | 1.2159 | 2 | NIBS 2003, Table A.8.1, Table 15B.5
52 | Horizontal Pump | DS4 Complete | no | Lognormal | 1.8 | 0 | 0.6 | 0.95 | 0 | NA | null | null | Normal | Normal | 77.1429 | 2.4318 | 4 | Not Available.
53 | Vertical Pump | DS1 Slight | no | Lognormal | 0.6 | 0 | 0.6 | 0.2 | 0.95 | NA | null | null | Normal | Normal | 5 | 0.30398 | 0.5 | Not Available.
54 | Vertical Pump | DS2 Moderate | no | Lognormal | 0.85 | 0 | 0.6 | 0.45 | 0.75 | NA | null | null | Normal | Normal | 17 | 0.60796 | 1 | Not Available.
55 | Vertical Pump | DS3 Extensive | no | Lognormal | 1.25 | 0 | 0.6 | 0.75 | 0.3 | NA | null | null | Normal | Normal | 37 | 1.2159 | 2 | NIBS 2003, Table A.8.1, Table 15B.5
56 | Vertical Pump | DS4 Complete | no | Lognormal | 1.5 | 0 | 0.6 | 0.95 | 0 | NA | null | null | Normal | Normal | 77.1429 | 2.4318 | 4 | Not Available.
57 | Buildings | DS1 Slight | no | Lognormal | 0.28 | 0 | 0.73 | 0.1 | 0.95 | NA | null | null | Normal | Normal | 5 | 0.60796 | 1 | NIBS 2003, Table A.8.1, Table 15B.5
58 | Buildings | DS2 Moderate | no | Lognormal | 0.72 | 0 | 0.73 | 0.4 | 0.75 | NA | null | null | Normal | Normal | 20 | 1.2159 | 2 | NIBS 2003, Table A.8.1, Table 15B.5
59 | Buildings | DS3 Extensive | no | Lognormal | 1.66 | 0 | 0.73 | 0.8 | 0.3 | NA | null | null | Normal | Normal | 50 | 2.4318 | 4 | NIBS 2003, Table A.8.1, Table 15B.5
60 | Buildings | DS4 Complete | no | Lognormal | 2.17 | 0 | 0.73 | 1 | 0 | NA | null | null | Normal | Normal | 102.8571 | 4.8637 | 8 | NIBS 2003, Table A.8.1, Table 15B.5
61 | Wells | DS1 Slight | no | Lognormal | 0.15 | 0 | 0.75 | 0.2 | 0.95 | NA | null | null | Normal | Normal | 5 | 0.30398 | 0.5 | NIBS 2003, Table 8.8
62 | Wells | DS2 Moderate | no | Lognormal | 0.36 | 0 | 0.65 | 0.45 | 0.75 | NA | null | null | Normal | Normal | 17 | 0.60796 | 1 | NIBS 2003, Table 8.8
63 | Wells | DS3 Extensive | no | Lognormal | 0.72 | 0 | 0.65 | 0.75 | 0.3 | NA | null | null | Normal | Normal | 37 | 1.2159 | 2 | NIBS 2003, Table 8.8
64 | Wells | DS4 Complete | no | Lognormal | 1.5 | 0 | 0.8 | 0.95 | 0 | NA | null | null | Normal | Normal | 77.1429 | 2.4318 | 4 | NIBS 2003, Table 8.8
65 | SYSTEM_OUTPUT | DS1 Slight | no | Lognormal | 10 | 0 | 1 | 0 | 1 | NA | null | null | Normal | Normal | 5 | 0.30398 | 0.5 | Unbreakable - Model Artifact
66 | SYSTEM_OUTPUT | DS2 Moderate | no | Lognormal | 10 | 0 | 1 | 0 | 1 | NA | null | null | Normal | Normal | 17 | 0.60796 | 1 | Unbreakable - Model Artifact
67 | SYSTEM_OUTPUT | DS3 Extensive | no | Lognormal | 10 | 0 | 1 | 0 | 1 | NA | null | null | Normal | Normal | 37 | 1.2159 | 2 | Unbreakable - Model Artifact
68 | SYSTEM_OUTPUT | DS4 Complete | no | Lognormal | 10 | 0 | 1 | 0 | 1 | NA | null | null | Normal | Normal | 77.1429 | 2.4318 | 4 | Unbreakable - Model Artifact

## damage_state_def
component_type | damage_state | damage_state_definition
backup_power_supply | DS1 Slight | not available
backup_power_supply | DS2 Moderate | not available
backup_power_supply | DS3 Extensive | not available
backup_power_supply | DS4 Complete | not available
chem_tank_coag1 | DS1 Slight | not available
chem_tank_coag1 | DS2 Moderate | not available
chem_tank_coag1 | DS3 Extensive | not available
chem_tank_coag1 | DS4 Complete | not available
chem_tank_Fl | DS1 Slight | not available
chem_tank_Fl | DS2 Moderate | not available
chem_tank_Fl | DS3 Extensive | not available
chem_tank_Fl | DS4 Complete | not available
chem_tank_ph_acid | DS1 Slight | not available
chem_tank_ph_acid | DS2 Moderate | not available
chem_tank_ph_acid | DS3 Extensive | not available
chem_tank_ph_acid | DS4 Complete | not available
chem_tank_ph_base | DS1 Slight | not available
chem_tank_ph_base | DS2 Moderate | not available
chem_tank_ph_base | DS3 Extensive | not available
chem_tank_ph_base | DS4 Complete | not available
chem_tank_phosphate | DS1 Slight | not available
chem_tank_phosphate | DS2 Moderate | not available
chem_tank_phosphate | DS3 Extensive | not available
chem_tank_phosphate | DS4 Complete | not available
chlorine_contact_chamber | DS1 Slight | not available
chlorine_contact_chamber | DS2 Moderate | not available
chlorine_contact_chamber | DS3 Extensive | not available
chlorine_contact_chamber | DS4 Complete | not available
chlorine_tank | DS1 Slight | not available
chlorine_tank | DS2 Moderate | not available
chlorine_tank | DS3 Extensive | not available
chlorine_tank | DS4 Complete | not available
clearwell_1 | DS1 Slight | not available
clearwell_1 | DS2 Moderate | not available
clearwell_1 | DS3 Extensive | not available
clearwell_1 | DS4 Complete | not available
clearwell_2 | DS1 Slight | not available
clearwell_2 | DS2 Moderate | not available
clearwell_2 | DS3 Extensive | not available
clearwell_2 | DS4 Complete | not available
commercial_power_supply | DS1 Slight | not available
commercial_power_supply | DS2 Moderate | not available
commercial_power_supply | DS3 Extensive | not available
commercial_power_supply | DS4 Complete | not available
connector_clearwell | DS1 Slight | not available
connector_clearwell | DS2 Moderate | not available
connector_clearwell | DS3 Extensive | not available
connector_clearwell | DS4 Complete | not available
connector_daf | DS1 Slight | not available
connector_daf | DS2 Moderate | not available
connector_daf | DS3 Extensive | not available
connector_daf | DS4 Complete | not available
connector_oz | DS1 Slight | not available
connector_oz | DS2 Moderate | not available
connector_oz | DS3 Extensive | not available
connector_oz | DS4 Complete | not available
daf_1 | DS1 Slight | not available
daf_1 | DS2 Moderate | not available
daf_1 | DS3 Extensive | not available
daf_1 | DS4 Complete | not available
daf_2 | DS1 Slight | not available
daf_2 | DS2 Moderate | not available
daf_2 | DS3 Extensive | not available
daf_2 | DS4 Complete | not available
daf_3 | DS1 Slight | not available
daf_3 | DS2 Moderate | not available
daf_3 | DS3 Extensive | not available
daf_3 | DS4 Complete | not available
daf_4 | DS1 Slight | not available
daf_4 | DS2 Moderate | not available
daf_4 | DS3 Extensive | not available
daf_4 | DS4 Complete | not available
daf_5 | DS1 Slight | not available
daf_5 | DS2 Moderate | not available
daf_5 | DS3 Extensive | not available
daf_5 | DS4 Complete | not available
daf_6 | DS1 Slight | not available
daf_6 | DS2 Moderate | not available
daf_6 | DS3 Extensive | not available
daf_6 | DS4 Complete | not available
daf_7 | DS1 Slight | not available
daf_7 | DS2 Moderate | not available
daf_7 | DS3 Extensive | not available
daf_7 | DS4 Complete | not available
daf_8 | DS1 Slight | not available
daf_8 | DS2 Moderate | not available
daf_8 | DS3 Extensive | not available
daf_8 | DS4 Complete | not available
feed_pump | DS1 Slight | not available
feed_pump | DS2 Moderate | not available
feed_pump | DS3 Extensive | not available
feed_pump | DS4 Complete | not available
filter_tank_1 | DS1 Slight | not available
filter_tank_1 | DS2 Moderate | not available
filter_tank_1 | DS3 Extensive | not available
filter_tank_1 | DS4 Complete | not available
filter_tank_2 | DS1 Slight | not available
filter_tank_2 | DS2 Moderate | not available
filter_tank_2 | DS3 Extensive | not available
filter_tank_2 | DS4 Complete | not available
filter_tank_3 | DS1 Slight | not available
filter_tank_3 | DS2 Moderate | not available
filter_tank_3 | DS3 Extensive | not available
filter_tank_3 | DS4 Complete | not available
filter_tank_4 | DS1 Slight | not available
filter_tank_4 | DS2 Moderate | not available
filter_tank_4 | DS3 Extensive | not available
filter_tank_4 | DS4 Complete | not available
filter_tank_5 | DS1 Slight | not available
filter_tank_5 | DS2 Moderate | not available
filter_tank_5 | DS3 Extensive | not available
filter_tank_5 | DS4 Complete | not available
filter_tank_6 | DS1 Slight | not available
filter_tank_6 | DS2 Moderate | not available
filter_tank_6 | DS3 Extensive | not available
filter_tank_6 | DS4 Complete | not available
filter_tank_7 | DS1 Slight | not available
filter_tank_7 | DS2 Moderate | not available
filter_tank_7 | DS3 Extensive | not available
filter_tank_7 | DS4 Complete | not available
filter_tank_8 | DS1 Slight | not available
filter_tank_8 | DS2 Moderate | not available
filter_tank_8 | DS3 Extensive | not available
filter_tank_8 | DS4 Complete | not available
floc_basin_1 | DS1 Slight | not available
floc_basin_1 | DS2 Moderate | not available
floc_basin_1 | DS3 Extensive | not available
floc_basin_1 | DS4 Complete | not available
floc_basin_2 | DS1 Slight | not available
floc_basin_2 | DS2 Moderate | not available
floc_basin_2 | DS3 Extensive | not available
floc_basin_2 | DS4 Complete | not available
floc_basin_3 | DS1 Slight | not available
floc_basin_3 | DS2 Moderate | not available
floc_basin_3 | DS3 Extensive | not available
floc_basin_3 | DS4 Complete | not available
floc_basin_4 | DS1 Slight | not available
floc_basin_4 | DS2 Moderate | not available
floc_basin_4 | DS3 Extensive | not available
floc_basin_4 | DS4 Complete | not available
floc_basin_5 | DS1 Slight | not available
floc_basin_5 | DS2 Moderate | not available
floc_basin_5 | DS3 Extensive | not available
floc_basin_5 | DS4 Complete | not available
floc_basin_6 | DS1 Slight | not available
floc_basin_6 | DS2 Moderate | not available
floc_basin_6 | DS3 Extensive | not available
floc_basin_6 | DS4 Complete | not available
floc_basin_7 | DS1 Slight | not available
floc_basin_7 | DS2 Moderate | not available
floc_basin_7 | DS3 Extensive | not available
floc_basin_7 | DS4 Complete | not available
floc_basin_8 | DS1 Slight | not available
floc_basin_8 | DS2 Moderate | not available
floc_basin_8 | DS3 Extensive | not available
floc_basin_8 | DS4 Complete | not available
input_pipe_1 | DS1 Slight | not available
input_pipe_1 | DS2 Moderate | not available
input_pipe_1 | DS3 Extensive | not available
input_pipe_1 | DS4 Complete | not available
output_1 | DS1 Slight | not available
output_1 | DS2 Moderate | not available
output_1 | DS3 Extensive | not available
output_1 | DS4 Complete | not available
output_2 | DS1 Slight | not available
output_2 | DS2 Moderate | not available
output_2 | DS3 Extensive | not available
output_2 | DS4 Complete | not available
ozone_contact_1 | DS1 Slight | not available
ozone_contact_1 | DS2 Moderate | not available
ozone_contact_1 | DS3 Extensive | not available
ozone_contact_1 | DS4 Complete | not available
ozone_contact_2 | DS1 Slight | not available
ozone_contact_2 | DS2 Moderate | not available
ozone_contact_2 | DS3 Extensive | not available
ozone_contact_2 | DS4 Complete | not available
ozone_gen | DS1 Slight | not available
ozone_gen | DS2 Moderate | not available
ozone_gen | DS3 Extensive | not available
ozone_gen | DS4 Complete | not available
pipe_ccc_1 | DS1 Slight | not available
pipe_ccc_1 | DS2 Moderate | not available
pipe_ccc_1 | DS3 Extensive | not available
pipe_ccc_1 | DS4 Complete | not available
pipe_connector_cw | DS1 Slight | not available
pipe_connector_cw | DS2 Moderate | not available
pipe_connector_cw | DS3 Extensive | not available
pipe_connector_cw | DS4 Complete | not available
pipe_connector_uv_out | DS1 Slight | not available
pipe_connector_uv_out | DS2 Moderate | not available
pipe_connector_uv_out | DS3 Extensive | not available
pipe_connector_uv_out | DS4 Complete | not available
pipe_cw_out_1 | DS1 Slight | not available
pipe_cw_out_1 | DS2 Moderate | not available
pipe_cw_out_1 | DS3 Extensive | not available
pipe_cw_out_1 | DS4 Complete | not available
pipe_cw_out_2 | DS1 Slight | not available
pipe_cw_out_2 | DS2 Moderate | not available
pipe_cw_out_2 | DS3 Extensive | not available
pipe_cw_out_2 | DS4 Complete | not available
pipe_fb_1 | DS1 Slight | not available
pipe_fb_1 | DS2 Moderate | not available
pipe_fb_1 | DS3 Extensive | not available
pipe_fb_1 | DS4 Complete | not available
pipe_fb_2 | DS1 Slight | not available
pipe_fb_2 | DS2 Moderate | not available
pipe_fb_2 | DS3 Extensive | not available
pipe_fb_2 | DS4 Complete | not available
pipe_fb_3 | DS1 Slight | not available
pipe_fb_3 | DS2 Moderate | not available
pipe_fb_3 | DS3 Extensive | not available
pipe_fb_3 | DS4 Complete | not available
pipe_fb_4 | DS1 Slight | not available
pipe_fb_4 | DS2 Moderate | not available
pipe_fb_4 | DS3 Extensive | not available
pipe_fb_4 | DS4 Complete | not available
pipe_fb_5 | DS1 Slight | not available
pipe_fb_5 | DS2 Moderate | not available
pipe_fb_5 | DS3 Extensive | not available
pipe_fb_5 | DS4 Complete | not available
pipe_fb_6 | DS1 Slight | not available
pipe_fb_6 | DS2 Moderate | not available
pipe_fb_6 | DS3 Extensive | not available
pipe_fb_6 | DS4 Complete | not available
pipe_fb_7 | DS1 Slight | not available
pipe_fb_7 | DS2 Moderate | not available
pipe_fb_7 | DS3 Extensive | not available
pipe_fb_7 | DS4 Complete | not available
pipe_fb_8 | DS1 Slight | not available
pipe_fb_8 | DS2 Moderate | not available
pipe_fb_8 | DS3 Extensive | not available
pipe_fb_8 | DS4 Complete | not available
pipe_ft_1 | DS1 Slight | not available
pipe_ft_1 | DS2 Moderate | not available
pipe_ft_1 | DS3 Extensive | not available
pipe_ft_1 | DS4 Complete | not available
pipe_ft_2 | DS1 Slight | not available
pipe_ft_2 | DS2 Moderate | not available
pipe_ft_2 | DS3 Extensive | not available
pipe_ft_2 | DS4 Complete | not available
pipe_ft_3 | DS1 Slight | not available
pipe_ft_3 | DS2 Moderate | not available
pipe_ft_3 | DS3 Extensive | not available
pipe_ft_3 | DS4 Complete | not available
pipe_ft_4 | DS1 Slight | not available
pipe_ft_4 | DS2 Moderate | not available
pipe_ft_4 | DS3 Extensive | not available
pipe_ft_4 | DS4 Complete | not available
pipe_ft_5 | DS1 Slight | not available
pipe_ft_5 | DS2 Moderate | not available
pipe_ft_5 | DS3 Extensive | not available
pipe_ft_5 | DS4 Complete | not available
pipe_ft_6 | DS1 Slight | not available
pipe_ft_6 | DS2 Moderate | not available
pipe_ft_6 | DS3 Extensive | not available
pipe_ft_6 | DS4 Complete | not available
pipe_ft_7 | DS1 Slight | not available
pipe_ft_7 | DS2 Moderate | not available
pipe_ft_7 | DS3 Extensive | not available
pipe_ft_7 | DS4 Complete | not available
pipe_ft_8 | DS1 Slight | not available
pipe_ft_8 | DS2 Moderate | not available
pipe_ft_8 | DS3 Extensive | not available
pipe_ft_8 | DS4 Complete | not available
pipe_ft_out_1 | DS1 Slight | not available
pipe_ft_out_1 | DS2 Moderate | not available
pipe_ft_out_1 | DS3 Extensive | not available
pipe_ft_out_1 | DS4 Complete | not available
pipe_large_fl_1 | DS1 Slight | not available
pipe_large_fl_1 | DS2 Moderate | not available
pipe_large_fl_1 | DS3 Extensive | not available
pipe_large_fl_1 | DS4 Complete | not available
pipe_large_fl_2 | DS1 Slight | not available
pipe_large_fl_2 | DS2 Moderate | not available
pipe_large_fl_2 | DS3 Extensive | not available
pipe_large_fl_2 | DS4 Complete | not available
pipe_oz_1 | DS1 Slight | not available
pipe_oz_1 | DS2 Moderate | not available
pipe_oz_1 | DS3 Extensive | not available
pipe_oz_1 | DS4 Complete | not available
pipe_oz_2 | DS1 Slight | not available
pipe_oz_2 | DS2 Moderate | not available
pipe_oz_2 | DS3 Extensive | not available
pipe_oz_2 | DS4 Complete | not available
pipe_to_clearwell | DS1 Slight | not available
pipe_to_clearwell | DS2 Moderate | not available
pipe_to_clearwell | DS3 Extensive | not available
pipe_to_clearwell | DS4 Complete | not available
pipe_to_distro_1 | DS1 Slight | not available
pipe_to_distro_1 | DS2 Moderate | not available
pipe_to_distro_1 | DS3 Extensive | not available
pipe_to_distro_1 | DS4 Complete | not available
pipe_to_distro_2 | DS1 Slight | not available
pipe_to_distro_2 | DS2 Moderate | not available
pipe_to_distro_2 | DS3 Extensive | not available
pipe_to_distro_2 | DS4 Complete | not available
pipe_uv_in_1 | DS1 Slight | not available
pipe_uv_in_1 | DS2 Moderate | not available
pipe_uv_in_1 | DS3 Extensive | not available
pipe_uv_in_1 | DS4 Complete | not available
pipe_uv_in_2 | DS1 Slight | not available
pipe_uv_in_2 | DS2 Moderate | not available
pipe_uv_in_2 | DS3 Extensive | not available
pipe_uv_in_2 | DS4 Complete | not available
pump_daf | DS1 Slight | not available
pump_daf | DS2 Moderate | not available
pump_daf | DS3 Extensive | not available
pump_daf | DS4 Complete | not available
uv_chamber_1 | DS1 Slight | not available
uv_chamber_1 | DS2 Moderate | not available
uv_chamber_1 | DS3 Extensive | not available
uv_chamber_1 | DS4 Complete | not available
uv_chamber_2 | DS1 Slight | not available
uv_chamber_2 | DS2 Moderate | not available
uv_chamber_2 | DS3 Extensive | not available
uv_chamber_2 | DS4 Complete | not available
uv_chamber_3 | DS1 Slight | not available
uv_chamber_3 | DS2 Moderate | not available
uv_chamber_3 | DS3 Extensive | not available
uv_chamber_3 | DS4 Complete | not available
uv_chamber_4 | DS1 Slight | not available
uv_chamber_4 | DS2 Moderate | not available
uv_chamber_4 | DS3 Extensive | not available
uv_chamber_4 | DS4 Complete | not available
uv_chamber_5 | DS1 Slight | not available
uv_chamber_5 | DS2 Moderate | not available
uv_chamber_5 | DS3 Extensive | not available
uv_chamber_5 | DS4 Complete | not available
uv_chamber_6 | DS1 Slight | not available
uv_chamber_6 | DS2 Moderate | not available
uv_chamber_6 | DS3 Extensive | not available
uv_chamber_6 | DS4 Complete | not available
well_1 | DS1 Slight | not available
well_1 | DS2 Moderate | not available
well_1 | DS3 Extensive | not available
well_1 | DS4 Complete | not available
well_2 | DS1 Slight | not available
well_2 | DS2 Moderate | not available
well_2 | DS3 Extensive | not available
well_2 | DS4 Complete | not available

## asset_names
Component Types | Synonyms
Baffles
Basins
Buildings
Chemical Tanks
Chlorination Equipment
Circular Clarification Tank
Electric Power Backup
Electric Power Commercial
Elevated Pipes
Flow Equalisation Basin
Grit Chamber
Horizontal Pump
Paddles
Power Station Gas Fired
Primary Clarifier Tank
Pump Station
Rectangular Sedimentation Tank
Reservoir
Scrapers
Secondary Treatment Tank
Sediment Flocculation
Sludge Digesters
Step Screens
Vertical Pump
Voltage Transformer
Wells
Internal Pipework
Pipe Connectors
SYSTEM_OUTPUT

## comps_to_add
pipe_to_processing