## table_description
table | description | note
component_list | This file lists the instances of various component types within the system. | Cost fractions define economic value of the individual component in relation to the system being under study. Must add up to 1.
component_connections | Network connections. Each pair of nodes is an edge. Directionality is defined by order of nodes in a row (Orig->Dest). | This file is used by network algorithm package to do the flow calculations. And Pygraphviz uses it to draw the system layout.
supply_setup | Capacity at the output nodes on the extremity of the component network
output_setup | Capacity at the output nodes on the extremity of the component network | Values given as percentages
comp_type_dmg_algo | List of component types with fragility and recovery data | Fragilities are defined according to discrete damage states. Recovery time is in Days.
damage_state_def

## component_list
component_id | component_type | component_class | cost_fraction | node_type | node_cluster | op_capacity
G1_SCPS | Generation Source | Generation Source | 0 | supply |  | 1
G2_SCPS | Generation Source | Generation Source | 0 | supply |  | 1
G3_SLPGC | Generation Source | Generation Source | 0 | supply |  | 1
G4_STA_RITA_L1 | Generation Source | Generation Source | 0 | supply |  | 1
G5_STA_RITA_L2 | Generation Source | Generation Source | 0 | supply |  | 1
CVT_230kv_01 | Capacitive Voltage Transformer 230kV | Voltage Transformer | 0.00093667 | transshipment | BAY83_A | 1
CVT_230kv_02 | Capacitive Voltage Transformer 230kV | Voltage Transformer | 0.00093667 | transshipment | BAY83_A | 1
CVT_230kv_03 | Capacitive Voltage Transformer 230kV | Voltage Transformer | 0.00093667 | transshipment | BAY83_A | 1
CVT_230kv_04 | Capacitive Voltage Transformer 230kV | Voltage Transformer | 0.00093667 | transshipment | BAY81_A | 1
CVT_230kv_05 | Capacitive Voltage Transformer 230kV | Voltage Transformer | 0.00093667 | transshipment | BAY81_A | 1
CVT_230kv_06 | Capacitive Voltage Transformer 230kV | Voltage Transformer | 0.00093667 | transshipment | BAY81_A | 1
CVT_230kv_07 | Capacitive Voltage Transformer 230kV | Voltage Transformer | 0.00093667 | transshipment | BAY86_A | 1
CVT_230kv_BUS_A | Capacitive Voltage Transformer 230kV | Voltage Transformer | 0.00093667 | transshipment |  | 1
CVT_230kv_BUS_B | Capacitive Voltage Transformer 230kV | Voltage Transformer | 0.00093667 | transshipment |  | 1
CVT_230kv_BACNO | Capacitive Voltage Transformer 230kV | Voltage Transformer | 0.00093667 | transshipment | BAY87_A | 1
CVT_230kv_AMAL2 | Capacitive Voltage Transformer 230kV | Voltage Transformer | 0.00093667 | transshipment | BAY84_A | 1
CVT_230kv_AMAL1 | Capacitive Voltage Transformer 230kV | Voltage Transformer | 0.00093667 | transshipment | BAY83_A | 1
CVT_230kv_BINAN | Capacitive Voltage Transformer 230kV | Voltage Transformer | 0.00093667 | transshipment | BAY82_A | 1
CVT_230kv_SROSA | Capacitive Voltage Transformer 230kV | Voltage Transformer | 0.00093667 | transshipment | BAY81_A | 1
CVT_230kv_RITA2 | Capacitive Voltage Transformer 230kV | Voltage Transformer | 0.00093667 | transshipment | BAY85_A | 1
CVT_230kv_RITA1 | Capacitive Voltage Transformer 230kV | Voltage Transformer | 0.00093667 | transshipment | BAY86_A | 1
CT_230kv_01 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY85 | 1
CT_230kv_02 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY85 | 1
CT_230kv_03 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY85 | 1
CT_230kv_04 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY85 | 1
CT_230kv_05 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY85 | 1
CT_230kv_06 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY85 | 1
CT_230kv_07 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY85 | 1
CT_230kv_08 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY85 | 1
CT_230kv_09 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY85 | 1
CT_230kv_10 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY85 | 1
CT_230kv_11 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY85 | 1
CT_230kv_12 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY86 | 1
CT_230kv_13 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY86 | 1
CT_230kv_14 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY86 | 1
CT_230kv_15 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY86 | 1
CT_230kv_16 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY86 | 1
CT_230kv_17 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY86 | 1
CT_230kv_18 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY86 | 1
CT_230kv_19 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY86 | 1
CT_230kv_20 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY86 | 1
CT_230kv_21 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY86 | 1
CT_230kv_22 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY86 | 1
CT_230kv_23 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY86 | 1
CT_230kv_24 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY86 | 1
CT_230kv_25 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY86 | 1
CT_230kv_26 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY86 | 1
CT_230kv_27 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY86 | 1
CT_230kv_28 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | SUBSTN69_L2 | 1
CT_230kv_29 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | SUBSTN69_L2 | 1
CT_230kv_30 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | SUBSTN69_L2 | 1
CT_230kv_31 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | SUBSTN69_L2 | 1
CT_230kv_32 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | SUBSTN69_L2 | 1
CT_230kv_33 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY87 | 1
CT_230kv_34 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY87 | 1
CT_230kv_35 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY87 | 1
CT_230kv_36 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY87 | 1
CT_230kv_37 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY87 | 1
CT_230kv_38 | Current Transformer 230kV | Current Transformer | 0.0012879 | transshipment | BAY87 | 1
DS_230kv_01 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | SUBSTN69_L4 | 1
DS_230kv_02 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | SUBSTN69_L2 | 1
DS_230kv_03 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY87 | 1
DS_230kv_04 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY87 | 1
DS_230kv_05 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY84 | 1
DS_230kv_06 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY84 | 1
DS_230kv_07 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY84 | 1
DS_230kv_08 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY84 | 1
DS_230kv_09 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY84 | 1
DS_230kv_10 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY84 | 1
DS_230kv_11 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY83 | 1
DS_230kv_12 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY83 | 1
DS_230kv_13 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY83 | 1
DS_230kv_14 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY83 | 1
DS_230kv_15 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY83 | 1
DS_230kv_16 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY83 | 1
DS_230kv_17 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY82 | 1
DS_230kv_18 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY82 | 1
DS_230kv_19 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY82 | 1
DS_230kv_20 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY82 | 1
DS_230kv_21 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY82 | 1
DS_230kv_22 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY82 | 1
DS_230kv_23 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY81 | 1
DS_230kv_24 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY81 | 1
DS_230kv_25 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY81 | 1
DS_230kv_26 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY81 | 1
DS_230kv_27 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY81 | 1
DS_230kv_28 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY81 | 1
DS_230kv_29 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY85 | 1
DS_230kv_30 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY85 | 1
DS_230kv_31 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY85 | 1
DS_230kv_32 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY85 | 1
DS_230kv_33 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY85 | 1
DS_230kv_34 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY85 | 1
DS_230kv_35 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY86 | 1
DS_230kv_36 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY86 | 1
DS_230kv_37 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY86 | 1
DS_230kv_38 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY86 | 1
DS_230kv_39 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY86 | 1
DS_230kv_40 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY86 | 1
DS_230kv_41 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY83_A | 1
DS_230kv_42 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY82_A | 1
DS_230kv_43 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY81_A | 1
DS_230kv_44 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY86 | 1
DS_230kv_45 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY87_A | 1
DS_230kv_46 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY84_A | 1
DS_230kv_47 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY83_A | 1
DS_230kv_48 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY82_A | 1
DS_230kv_49 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY81_A | 1
DS_230kv_50 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY85_A | 1
DS_230kv_51 | Disconnect Switch 230kV 3-Phase | Disconnect Switch | 0.0013933 | transshipment | BAY86_A | 1
LA_01 | Lightning Arrester | Lightning Arrester | 0.00035125 | transshipment | BAY87_A | 1
LA_02 | Lightning Arrester | Lightning Arrester | 0.00035125 | transshipment | BAY84_A | 1
LA_03 | Lightning Arrester | Lightning Arrester | 0.00035125 | transshipment | BAY83_A | 1
LA_04 | Lightning Arrester | Lightning Arrester | 0.00035125 | transshipment | BAY82_A | 1
LA_05 | Lightning Arrester | Lightning Arrester | 0.00035125 | transshipment | BAY81_A | 1
LA_06 | Lightning Arrester | Lightning Arrester | 0.00035125 | transshipment | BAY85_A | 1
LA_07 | Lightning Arrester | Lightning Arrester | 0.00035125 | transshipment | BAY86_A | 1
LA_08 | Lightning Arrester | Lightning Arrester | 0.00035125 | transshipment | SUBSTN69_L2 | 1
LA_09 | Lightning Arrester | Lightning Arrester | 0.00035125 | transshipment | SUBSTN69_L4 | 1
LA_10 | Lightning Arrester | Lightning Arrester | 0.00035125 | transshipment | BAY86_A | 1
PCB_230kv_3p_01 | Power Circuit Breaker 3-Phase 230kV with CTs | Circuit Breaker | 0.014518 | transshipment | BAY84 | 1
PCB_230kv_3p_02 | Power Circuit Breaker 3-Phase 230kV with CTs | Circuit Breaker | 0.014518 | transshipment | BAY84 | 1
PCB_230kv_3p_03 | Power Circuit Breaker 3-Phase 230kV with CTs | Circuit Breaker | 0.014518 | transshipment | BAY84 | 1
PCB_230kv_3p_04 | Power Circuit Breaker 3-Phase 230kV with CTs | Circuit Breaker | 0.014518 | transshipment | BAY83 | 1
PCB_230kv_3p_05 | Power Circuit Breaker 3-Phase 230kV with CTs | Circuit Breaker | 0.014518 | transshipment | BAY83 | 1
PCB_230kv_3p_06 | Power Circuit Breaker 3-Phase 230kV with CTs | Circuit Breaker | 0.014518 | transshipment | BAY83 | 1
PCB_230kv_3p_07 | Power Circuit Breaker 3-Phase 230kV with CTs | Circuit Breaker | 0.014518 | transshipment | BAY82 | 1
PCB_230kv_3p_08 | Power Circuit Breaker 3-Phase 230kV with CTs | Circuit Breaker | 0.014518 | transshipment | BAY82 | 1
PCB_230kv_3p_09 | Power Circuit Breaker 3-Phase 230kV with CTs | Circuit Breaker | 0.014518 | transshipment | BAY82 | 1
PCB_230kv_3p_10 | Power Circuit Breaker 3-Phase 230kV with CTs | Circuit Breaker | 0.014518 | transshipment | BAY81 | 1
PCB_230kv_3p_11 | Power Circuit Breaker 3-Phase 230kV with CTs | Circuit Breaker | 0.014518 | transshipment | BAY81 | 1
PCB_230kv_3p_12 | Power Circuit Breaker 3-Phase 230kV with CTs | Circuit Breaker | 0.014518 | transshipment | BAY81 | 1
PCB_230kv_1p_01 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY85 | 1
PCB_230kv_1p_02 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY85 | 1
PCB_230kv_1p_03 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY85 | 1
PCB_230kv_1p_04 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY85 | 1
PCB_230kv_1p_05 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY85 | 1
PCB_230kv_1p_06 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY85 | 1
PCB_230kv_1p_07 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY86 | 1
PCB_230kv_1p_08 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY86 | 1
PCB_230kv_1p_09 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY86 | 1
PCB_230kv_1p_10 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY86 | 1
PCB_230kv_1p_11 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY86 | 1
PCB_230kv_1p_12 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY86 | 1
PCB_230kv_1p_13 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY86 | 1
PCB_230kv_1p_14 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY86 | 1
PCB_230kv_1p_15 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY86 | 1
PCB_230kv_1p_16 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | SUBSTN69_L2 | 1
PCB_230kv_1p_17 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | SUBSTN69_L2 | 1
PCB_230kv_1p_18 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | SUBSTN69_L2 | 1
PCB_230kv_1p_19 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY87 | 1
PCB_230kv_1p_20 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY87 | 1
PCB_230kv_1p_21 | Power Circuit Breaker 1-Phase 230kV | Circuit Breaker | 0.007025 | transshipment | BAY87 | 1
PTR_100MVA | Power Transformer 100MVA 230/69 | Power Transformer | 0.15104 | transshipment | SUBSTN69_L2 | 1
PTR_50MVA | Power Transformer 50MVA 230/69 | Power Transformer | 0.13113 | transshipment | SUBSTN69_L4 | 1
BUS_230kV_A | Bus 230kV | Bus | 0 | transshipment |  | 1
BUS_230kV_B | Bus 230kV | Bus | 0 | transshipment |  | 1
CTRL_BLDG | Control Building With Equipment | Control Building | 0.25758 | dependency |  | 1
BACNOTAN_STEEL | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | BAY87_A | 1
CALACA_LOCAL | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | BAY87_B | 1
PHIL_STEEL_CORP | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | BAY84_B | 1
AMADEO_L2 | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | BAY84_A | 1
AMADEO_L1 | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | BAY83_A | 1
BINAN | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | BAY82_A | 1
STA_ROSA | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | BAY81_A | 1
SEM_CAL_ASSETS | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | BAY82_A | 1
XNODE_B83_A | CONN_NODE | JUNCTION POINT | 0 | transshipment | BAY83 | 1
XNODE_B83_B | CONN_NODE | JUNCTION POINT | 0 | transshipment | BAY83 | 1
XNODE_B81_A | CONN_NODE | JUNCTION POINT | 0 | transshipment | BAY81 | 1
XNODE_B81_B | CONN_NODE | JUNCTION POINT | 0 | transshipment | BAY81 | 1
XNODE_B84_A | CONN_NODE | JUNCTION POINT | 0 | transshipment | BAY84 | 1
XNODE_B84_B | CONN_NODE | JUNCTION POINT | 0 | transshipment | BAY84 | 1
XNODE_B82_A | CONN_NODE | JUNCTION POINT | 0 | transshipment | BAY82 | 1
XNODE_B82_B | CONN_NODE | JUNCTION POINT | 0 | transshipment | BAY82 | 1
XNODE_B85_A | CONN_NODE | JUNCTION POINT | 0 | transshipment | BAY85 | 1
XNODE_B86_A | CONN_NODE | JUNCTION POINT | 0 | transshipment | BAY86 | 1
XNODE_B86_B | CONN_NODE | JUNCTION POINT | 0 | transshipment | BAY86 | 1

## component_connections
origin | destination | link_capacity | weight
G1_SCPS | CVT_230kv_01 | 1 | 0
CVT_230kv_01 | CVT_230kv_02 | 1 | 0
CVT_230kv_02 | CVT_230kv_03 | 1 | 0
CVT_230kv_03 | DS_230kv_41 | 1 | 0
DS_230kv_41 | XNODE_B83_B | 1 | 0
XNODE_B83_B | DS_230kv_14 | 1 | 0
XNODE_B83_B | DS_230kv_15 | 1 | 0
DS_230kv_14 | XNODE_B83_B | 1 | 0
DS_230kv_15 | XNODE_B83_B | 1 | 0
DS_230kv_15 | PCB_230kv_3p_06 | 1 | 0
PCB_230kv_3p_06 | DS_230kv_15 | 1 | 0
PCB_230kv_3p_06 | DS_230kv_16 | 1 | 0
DS_230kv_16 | PCB_230kv_3p_06 | 1 | 0
DS_230kv_16 | BUS_230kV_B | 1 | 0
BUS_230kV_B | DS_230kv_16 | 1 | 0
DS_230kv_14 | PCB_230kv_3p_05 | 1 | 0
PCB_230kv_3p_05 | DS_230kv_14 | 1 | 0
PCB_230kv_3p_05 | DS_230kv_13 | 1 | 0
DS_230kv_13 | PCB_230kv_3p_05 | 1 | 0
DS_230kv_13 | XNODE_B83_A | 1 | 0
XNODE_B83_A | DS_230kv_13 | 1 | 0
XNODE_B83_A | DS_230kv_12 | 1 | 0
DS_230kv_12 | XNODE_B83_A | 1 | 0
XNODE_B83_A | DS_230kv_47 | 1 | 0
DS_230kv_47 | XNODE_B83_A | 1 | 0
CVT_230kv_BUS_A | BUS_230kV_A | 1 | 0
CVT_230kv_BUS_B | BUS_230kV_B | 1 | 0
LA_03 | DS_230kv_47 | 1 | 0
DS_230kv_47 | CVT_230kv_AMAL1 | 1 | 0
CVT_230kv_AMAL1 | AMADEO_L1 | 1 | 0
DS_230kv_12 | PCB_230kv_3p_04 | 1 | 0
PCB_230kv_3p_04 | DS_230kv_12 | 1 | 0
PCB_230kv_3p_04 | DS_230kv_11 | 1 | 0
DS_230kv_11 | PCB_230kv_3p_04 | 1 | 0
DS_230kv_11 | BUS_230kV_A | 1 | 0
BUS_230kV_A | DS_230kv_11 | 1 | 0
G2_SCPS | CVT_230kv_04 | 1 | 0
CVT_230kv_04 | CVT_230kv_05 | 1 | 0
CVT_230kv_05 | CVT_230kv_06 | 1 | 0
CVT_230kv_06 | DS_230kv_43 | 1 | 0
DS_230kv_43 | XNODE_B81_B | 1 | 0
XNODE_B81_B | DS_230kv_26 | 1 | 0
XNODE_B81_B | DS_230kv_27 | 1 | 0
DS_230kv_26 | XNODE_B81_B | 1 | 0
DS_230kv_27 | XNODE_B81_B | 1 | 0
DS_230kv_27 | PCB_230kv_3p_12 | 1 | 0
PCB_230kv_3p_12 | DS_230kv_27 | 1 | 0
PCB_230kv_3p_12 | DS_230kv_28 | 1 | 0
DS_230kv_28 | PCB_230kv_3p_12 | 1 | 0
DS_230kv_28 | BUS_230kV_B | 1 | 0
BUS_230kV_B | DS_230kv_28 | 1 | 0
DS_230kv_26 | PCB_230kv_3p_11 | 1 | 0
PCB_230kv_3p_11 | DS_230kv_26 | 1 | 0
PCB_230kv_3p_11 | DS_230kv_25 | 1 | 0
DS_230kv_25 | PCB_230kv_3p_11 | 1 | 0
DS_230kv_25 | XNODE_B81_A | 1 | 0
XNODE_B81_A | DS_230kv_25 | 1 | 0
XNODE_B81_A | DS_230kv_24 | 1 | 0
DS_230kv_24 | XNODE_B81_A | 1 | 0
XNODE_B81_A | DS_230kv_49 | 1 | 0
DS_230kv_49 | XNODE_B81_A | 1 | 0
LA_05 | DS_230kv_49 | 1 | 0
DS_230kv_49 | CVT_230kv_SROSA | 1 | 0
CVT_230kv_SROSA | STA_ROSA | 1 | 0
DS_230kv_24 | PCB_230kv_3p_10 | 1 | 0
PCB_230kv_3p_10 | DS_230kv_24 | 1 | 0
PCB_230kv_3p_10 | DS_230kv_23 | 1 | 0
DS_230kv_23 | BUS_230kV_A | 1 | 0
BUS_230kV_A | DS_230kv_23 | 1 | 0
BUS_230kV_A | DS_230kv_03 | 1 | 0
DS_230kv_03 | BUS_230kV_A | 1 | 0
DS_230kv_03 | CT_230kv_33 | 1 | 0
CT_230kv_33 | DS_230kv_03 | 1 | 0
CT_230kv_33 | CT_230kv_34 | 1 | 0
CT_230kv_34 | CT_230kv_33 | 1 | 0
CT_230kv_34 | CT_230kv_35 | 1 | 0
CT_230kv_35 | CT_230kv_34 | 1 | 0
CT_230kv_35 | PCB_230kv_1p_19 | 1 | 0
PCB_230kv_1p_19 | CT_230kv_35 | 1 | 0
PCB_230kv_1p_19 | PCB_230kv_1p_20 | 1 | 0
PCB_230kv_1p_20 | PCB_230kv_1p_19 | 1 | 0
PCB_230kv_1p_20 | PCB_230kv_1p_21 | 1 | 0
PCB_230kv_1p_21 | PCB_230kv_1p_20 | 1 | 0
PCB_230kv_1p_21 | CT_230kv_36 | 1 | 0
CT_230kv_36 | PCB_230kv_1p_21 | 1 | 0
CT_230kv_36 | CT_230kv_37 | 1 | 0
CT_230kv_37 | CT_230kv_36 | 1 | 0
CT_230kv_37 | CT_230kv_38 | 1 | 0
CT_230kv_38 | CT_230kv_37 | 1 | 0
CT_230kv_38 | DS_230kv_04 | 1 | 0
DS_230kv_04 | CT_230kv_38 | 1 | 0
DS_230kv_04 | DS_230kv_45 | 1 | 0
DS_230kv_45 | DS_230kv_04 | 1 | 0
LA_01 | DS_230kv_45 | 1 | 0
DS_230kv_45 | CVT_230kv_BACNO | 1 | 0
CVT_230kv_BACNO | BACNOTAN_STEEL | 1 | 0
BUS_230kV_A | DS_230kv_05 | 1 | 0
DS_230kv_05 | BUS_230kV_A | 1 | 0
DS_230kv_05 | PCB_230kv_3p_01 | 1 | 0
PCB_230kv_3p_01 | DS_230kv_05 | 1 | 0
PCB_230kv_3p_01 | DS_230kv_06 | 1 | 0
DS_230kv_06 | PCB_230kv_3p_01 | 1 | 0
DS_230kv_06 | XNODE_B84_A | 1 | 0
XNODE_B84_A | DS_230kv_06 | 1 | 0
XNODE_B84_A | DS_230kv_46 | 1 | 0
DS_230kv_46 | XNODE_B84_A | 1 | 0
LA_02 | CVT_230kv_AMAL2 | 1 | 0
DS_230kv_46 | CVT_230kv_AMAL2 | 1 | 0
CVT_230kv_AMAL2 | AMADEO_L2 | 1 | 0
XNODE_B84_A | DS_230kv_07 | 1 | 0
DS_230kv_07 | XNODE_B84_A | 1 | 0
DS_230kv_07 | PCB_230kv_3p_02 | 1 | 0
PCB_230kv_3p_02 | DS_230kv_07 | 1 | 0
PCB_230kv_3p_02 | DS_230kv_08 | 1 | 0
DS_230kv_08 | PCB_230kv_3p_02 | 1 | 0
DS_230kv_08 | XNODE_B84_B | 1 | 0
XNODE_B84_B | DS_230kv_08 | 1 | 0
XNODE_B84_B | DS_230kv_09 | 1 | 0
DS_230kv_09 | XNODE_B84_B | 1 | 0
DS_230kv_09 | PCB_230kv_3p_03 | 1 | 0
PCB_230kv_3p_03 | DS_230kv_09 | 1 | 0
PCB_230kv_3p_03 | DS_230kv_10 | 1 | 0
DS_230kv_10 | PCB_230kv_3p_03 | 1 | 0
DS_230kv_10 | BUS_230kV_B | 1 | 0
BUS_230kV_B | DS_230kv_10 | 1 | 0
XNODE_B84_B | DS_230kv_01 | 1 | 0
DS_230kv_01 | XNODE_B84_B | 1 | 0
LA_09 | DS_230kv_01 | 1 | 0
DS_230kv_01 | PTR_50MVA | 1 | 0
PTR_50MVA | PHIL_STEEL_CORP | 1 | 0
BUS_230kV_A | DS_230kv_02 | 1 | 0
DS_230kv_02 | PCB_230kv_1p_16 | 1 | 0
PCB_230kv_1p_16 | PCB_230kv_1p_17 | 1 | 0
PCB_230kv_1p_17 | PCB_230kv_1p_18 | 1 | 0
PCB_230kv_1p_18 | CT_230kv_28 | 1 | 0
CT_230kv_28 | CT_230kv_29 | 1 | 0
CT_230kv_29 | CT_230kv_30 | 1 | 0
CT_230kv_30 | CT_230kv_31 | 1 | 0
CT_230kv_31 | CT_230kv_32 | 1 | 0
CT_230kv_32 | PTR_100MVA | 1 | 0
LA_08 | PTR_100MVA | 1 | 0
PTR_100MVA | CALACA_LOCAL | 1 | 0
BUS_230kV_A | DS_230kv_17 | 1 | 0
DS_230kv_17 | BUS_230kV_A | 1 | 0
DS_230kv_17 | PCB_230kv_3p_07 | 1 | 0
PCB_230kv_3p_07 | DS_230kv_17 | 1 | 0
PCB_230kv_3p_07 | DS_230kv_18 | 1 | 0
DS_230kv_18 | PCB_230kv_3p_07 | 1 | 0
DS_230kv_18 | XNODE_B82_A | 1 | 0
XNODE_B82_A | DS_230kv_18 | 1 | 0
XNODE_B82_A | DS_230kv_19 | 1 | 0
DS_230kv_19 | XNODE_B82_A | 1 | 0
DS_230kv_19 | PCB_230kv_3p_08 | 1 | 0
PCB_230kv_3p_08 | DS_230kv_19 | 1 | 0
PCB_230kv_3p_08 | DS_230kv_20 | 1 | 0
DS_230kv_20 | PCB_230kv_3p_08 | 1 | 0
DS_230kv_20 | XNODE_B82_B | 1 | 0
XNODE_B82_B | DS_230kv_20 | 1 | 0
XNODE_B82_B | DS_230kv_21 | 1 | 0
DS_230kv_21 | XNODE_B82_B | 1 | 0
DS_230kv_21 | PCB_230kv_3p_09 | 1 | 0
PCB_230kv_3p_09 | DS_230kv_21 | 1 | 0
PCB_230kv_3p_09 | DS_230kv_22 | 1 | 0
DS_230kv_22 | PCB_230kv_3p_09 | 1 | 0
DS_230kv_22 | BUS_230kV_B | 1 | 0
BUS_230kV_B | DS_230kv_22 | 1 | 0
XNODE_B82_A | DS_230kv_48 | 1 | 0
DS_230kv_48 | XNODE_B82_A | 1 | 0
DS_230kv_48 | CVT_230kv_BINAN | 1 | 0
LA_04 | CVT_230kv_BINAN | 1 | 0
CVT_230kv_BINAN | BINAN | 1 | 0
XNODE_B82_B | DS_230kv_42 | 1 | 0
DS_230kv_42 | SEM_CAL_ASSETS | 1 | 0
BUS_230kV_A | DS_230kv_29 | 1 | 0
DS_230kv_29 | BUS_230kV_A | 1 | 0
DS_230kv_29 | CT_230kv_01 | 1 | 0
CT_230kv_01 | CT_230kv_02 | 1 | 0
CT_230kv_02 | CT_230kv_01 | 1 | 0
CT_230kv_02 | CT_230kv_03 | 1 | 0
CT_230kv_03 | CT_230kv_02 | 1 | 0
CT_230kv_03 | CT_230kv_04 | 1 | 0
CT_230kv_04 | CT_230kv_03 | 1 | 0
CT_230kv_04 | CT_230kv_05 | 1 | 0
CT_230kv_05 | CT_230kv_04 | 1 | 0
CT_230kv_05 | PCB_230kv_1p_01 | 1 | 0
PCB_230kv_1p_01 | CT_230kv_05 | 1 | 0
PCB_230kv_1p_01 | PCB_230kv_1p_02 | 1 | 0
PCB_230kv_1p_02 | PCB_230kv_1p_01 | 1 | 0
PCB_230kv_1p_02 | PCB_230kv_1p_03 | 1 | 0
PCB_230kv_1p_03 | PCB_230kv_1p_02 | 1 | 0
PCB_230kv_1p_03 | DS_230kv_30 | 1 | 0
DS_230kv_30 | PCB_230kv_1p_03 | 1 | 0
G5_STA_RITA_L2 | CVT_230kv_RITA2 | 1 | 0
LA_06 | CVT_230kv_RITA2 | 1 | 0
CVT_230kv_RITA2 | DS_230kv_50 | 1 | 0
DS_230kv_50 | XNODE_B85_A | 1 | 0
XNODE_B85_A | DS_230kv_30 | 1 | 0
XNODE_B85_A | DS_230kv_31 | 1 | 0
DS_230kv_30 | XNODE_B85_A | 1 | 0
DS_230kv_31 | XNODE_B85_A | 1 | 0
DS_230kv_31 | CT_230kv_06 | 1 | 0
CT_230kv_06 | DS_230kv_31 | 1 | 0
CT_230kv_06 | CT_230kv_07 | 1 | 0
CT_230kv_07 | CT_230kv_06 | 1 | 0
CT_230kv_07 | CT_230kv_08 | 1 | 0
CT_230kv_08 | CT_230kv_07 | 1 | 0
CT_230kv_08 | PCB_230kv_1p_04 | 1 | 0
PCB_230kv_1p_04 | CT_230kv_08 | 1 | 0
PCB_230kv_1p_04 | PCB_230kv_1p_05 | 1 | 0
PCB_230kv_1p_05 | PCB_230kv_1p_04 | 1 | 0
PCB_230kv_1p_05 | PCB_230kv_1p_06 | 1 | 0
PCB_230kv_1p_06 | PCB_230kv_1p_05 | 1 | 0
PCB_230kv_1p_06 | CT_230kv_09 | 1 | 0
CT_230kv_09 | PCB_230kv_1p_06 | 1 | 0
CT_230kv_09 | CT_230kv_10 | 1 | 0
CT_230kv_10 | CT_230kv_09 | 1 | 0
CT_230kv_10 | CT_230kv_11 | 1 | 0
CT_230kv_11 | CT_230kv_10 | 1 | 0
CT_230kv_11 | DS_230kv_32 | 1 | 0
DS_230kv_32 | CT_230kv_11 | 1 | 0
DS_230kv_32 | DS_230kv_33 | 1 | 0
DS_230kv_33 | DS_230kv_32 | 1 | 0
DS_230kv_33 | DS_230kv_34 | 1 | 0
DS_230kv_34 | DS_230kv_33 | 1 | 0
DS_230kv_34 | BUS_230kV_B | 1 | 0
BUS_230kV_B | DS_230kv_34 | 1 | 0
BUS_230kV_A | DS_230kv_35 | 1 | 0
DS_230kv_35 | BUS_230kV_A | 1 | 0
DS_230kv_35 | CT_230kv_12 | 1 | 0
CT_230kv_12 | DS_230kv_35 | 1 | 0
CT_230kv_12 | CT_230kv_13 | 1 | 0
CT_230kv_13 | CT_230kv_12 | 1 | 0
CT_230kv_13 | CT_230kv_14 | 1 | 0
CT_230kv_14 | CT_230kv_13 | 1 | 0
CT_230kv_14 | CT_230kv_15 | 1 | 0
CT_230kv_15 | CT_230kv_14 | 1 | 0
CT_230kv_15 | CT_230kv_16 | 1 | 0
CT_230kv_16 | CT_230kv_15 | 1 | 0
CT_230kv_16 | PCB_230kv_1p_07 | 1 | 0
PCB_230kv_1p_07 | CT_230kv_16 | 1 | 0
PCB_230kv_1p_07 | PCB_230kv_1p_08 | 1 | 0
PCB_230kv_1p_08 | PCB_230kv_1p_07 | 1 | 0
PCB_230kv_1p_08 | PCB_230kv_1p_09 | 1 | 0
PCB_230kv_1p_09 | PCB_230kv_1p_08 | 1 | 0
PCB_230kv_1p_09 | DS_230kv_36 | 1 | 0
DS_230kv_36 | PCB_230kv_1p_09 | 1 | 0
DS_230kv_36 | XNODE_B86_A | 1 | 0
G4_STA_RITA_L1 | CVT_230kv_RITA1 | 1 | 0
LA_07 | CVT_230kv_RITA1 | 1 | 0
CVT_230kv_RITA1 | DS_230kv_51 | 1 | 0
DS_230kv_51 | XNODE_B86_A | 1 | 0
XNODE_B86_A | DS_230kv_36 | 1 | 0
XNODE_B86_A | DS_230kv_37 | 1 | 0
DS_230kv_37 | XNODE_B86_A | 1 | 0
DS_230kv_37 | CT_230kv_17 | 1 | 0
CT_230kv_17 | DS_230kv_37 | 1 | 0
CT_230kv_17 | CT_230kv_18 | 1 | 0
CT_230kv_18 | CT_230kv_17 | 1 | 0
CT_230kv_18 | CT_230kv_19 | 1 | 0
CT_230kv_19 | CT_230kv_18 | 1 | 0
CT_230kv_19 | PCB_230kv_1p_10 | 1 | 0
PCB_230kv_1p_10 | CT_230kv_19 | 1 | 0
PCB_230kv_1p_10 | PCB_230kv_1p_11 | 1 | 0
PCB_230kv_1p_11 | PCB_230kv_1p_10 | 1 | 0
PCB_230kv_1p_11 | PCB_230kv_1p_12 | 1 | 0
PCB_230kv_1p_12 | PCB_230kv_1p_11 | 1 | 0
PCB_230kv_1p_12 | CT_230kv_20 | 1 | 0
CT_230kv_20 | PCB_230kv_1p_12 | 1 | 0
CT_230kv_20 | CT_230kv_21 | 1 | 0
CT_230kv_21 | CT_230kv_20 | 1 | 0
CT_230kv_21 | CT_230kv_22 | 1 | 0
CT_230kv_22 | CT_230kv_21 | 1 | 0
CT_230kv_22 | DS_230kv_38 | 1 | 0
DS_230kv_38 | CT_230kv_22 | 1 | 0
DS_230kv_38 | XNODE_B86_B | 1 | 0
XNODE_B86_B | DS_230kv_38 | 1 | 0
XNODE_B86_B | DS_230kv_39 | 1 | 0
DS_230kv_39 | XNODE_B86_B | 1 | 0
DS_230kv_39 | PCB_230kv_1p_13 | 1 | 0
PCB_230kv_1p_13 | DS_230kv_39 | 1 | 0
PCB_230kv_1p_13 | PCB_230kv_1p_14 | 1 | 0
PCB_230kv_1p_14 | PCB_230kv_1p_13 | 1 | 0
PCB_230kv_1p_14 | PCB_230kv_1p_15 | 1 | 0
PCB_230kv_1p_15 | PCB_230kv_1p_14 | 1 | 0
PCB_230kv_1p_15 | CT_230kv_23 | 1 | 0
CT_230kv_23 | PCB_230kv_1p_15 | 1 | 0
CT_230kv_23 | CT_230kv_24 | 1 | 0
CT_230kv_24 | CT_230kv_23 | 1 | 0
CT_230kv_24 | CT_230kv_25 | 1 | 0
CT_230kv_25 | CT_230kv_24 | 1 | 0
CT_230kv_25 | CT_230kv_26 | 1 | 0
CT_230kv_26 | CT_230kv_25 | 1 | 0
CT_230kv_26 | CT_230kv_27 | 1 | 0
CT_230kv_27 | CT_230kv_26 | 1 | 0
CT_230kv_27 | DS_230kv_40 | 1 | 0
DS_230kv_40 | CT_230kv_27 | 1 | 0
DS_230kv_40 | BUS_230kV_B | 1 | 0
BUS_230kV_B | DS_230kv_40 | 1 | 0
G3_SLPGC | CVT_230kv_07 | 1 | 0
LA_10 | CVT_230kv_07 | 1 | 0
CVT_230kv_07 | DS_230kv_44 | 1 | 0
DS_230kv_44 | CVT_230kv_07 | 1 | 0
DS_230kv_44 | XNODE_B86_B | 1 | 0
CTRL_BLDG | G1_SCPS | 1 | 0
CTRL_BLDG | G2_SCPS | 1 | 0
CTRL_BLDG | G3_SLPGC | 1 | 0
CTRL_BLDG | G4_STA_RITA_L1 | 1 | 0
CTRL_BLDG | G5_STA_RITA_L2 | 1 | 0
CTRL_BLDG | PHIL_STEEL_CORP | 1 | 0
CTRL_BLDG | CALACA_LOCAL | 1 | 0
CTRL_BLDG | SEM_CAL_ASSETS | 1 | 0
CTRL_BLDG | BACNOTAN_STEEL | 1 | 0
CTRL_BLDG | AMADEO_L2 | 1 | 0
CTRL_BLDG | AMADEO_L1 | 1 | 0
CTRL_BLDG | BINAN | 1 | 0
CTRL_BLDG | STA_ROSA | 1 | 0

## supply_setup
input_node | input_capacity | capacity_fraction | commodity_type
G1_SCPS | 300 | 0.16835 | electricity
G2_SCPS | 300 | 0.16835 | electricity
G3_SLPGC | 0 | 0 | electricity
G4_STA_RITA_L1 | 330 | 0.18519 | electricity
G5_STA_RITA_L2 | 852 | 0.47811 | electricity
Note on B5: Maruf Rahman: Value adjusted to match demand. It it still lower than the max monthly average as of data for OCT '14 (370MW).

## output_setup
output_node | production_node | output_node_capacity | capacity_fraction | priority
PHIL_STEEL_CORP | PTR_50MVA | 4 | 0.0022447 | 8
CALACA_LOCAL | PTR_100MVA | 56 | 0.031425 | 7
SEM_CAL_ASSETS | DS_230kv_43 | 10 | 0.0056117 | 6
BACNOTAN_STEEL | CVT_230kv_BACNO | 64 | 0.035915 | 5
AMADEO_L2 | CVT_230kv_AMAL2 | 375 | 0.21044 | 2
AMADEO_L1 | CVT_230kv_AMAL1 | 402 | 0.22559 | 1
BINAN | CVT_230kv_BINAN | 424 | 0.23793 | 4
STA_ROSA | CVT_230kv_SROSA | 447 | 0.25084 | 3

## comp_type_dmg_algo
component_type | damage_state | damage_function | mode | median | beta | damage_lambda | damage_ratio | functionality | minimum | sigma_1 | sigma_2 | recovery_mean | recovery_std | recovery_95percentile | fragility_source
Capacitive Voltage Transformer 230kV | Failure | Lognormal | 1 | 0.6 | 0.26 | 0.18247 | 1 | 0 | NA | NA | NA | 21 | 4.26 | NA | Vanzi voltage transformer Syner-G Table 5.14
Capacitive Voltage Transformer 69kV | Failure | Lognormal | 1 | 0.6 | 0.25 | 0.18247 | 1 | 0 | NA | NA | NA | 21 | 4.26 | NA | Vanzi voltage transformer Syner-G Table 5.14
Current Transformer 230kV | Failure | Lognormal | 1 | 0.51 | 0.2 | -0.69 | 1 | 0 | NA | NA | NA | 21 | 4.26 | NA | Median mid-way between Vanzi current and voltage transformer with damage threshold just below 0.4g
Disconnect Switch 230kV 3-Phase | Failure | Lognormal | 1 | 0.6 | 0.28 | -0.29 | 0.3 | 0 | NA | NA | NA | 7 | 1.22 | NA | NGCP judgement derived through consensus at Infrastructure Symposium . Vulnerability corresponds closely with Vanzi horizontal disconnect (Syner-G Table 5.6).
Disconnect Switch 69kV 3-Phase | Failure | Lognormal | 1 | 0.96 | 0.43 | 0.18 | 0.3 | 0 | NA | NA | NA | 7 | 1.22 | NA | NGCP judgement derived through consensus at Infrastructure Symposium . Vulnerability corresponds closely with Vanzi horizontal disconnect (Syner-G Table 5.6) but shifted proportionately as per MN HAZUS curves in Tbale 5.7 of Syner-G (0.36g at medium with no change at threshold).
Lightning Arrester | Failure | Lognormal | 1 | 0.55 | 0.3 | 0.08 | 0.3 | 0 | NA | NA | NA | 5 | 0.61 | NA | Midway between Vanzi discharger and ligntning arrestor (Syner-G Table 5.4 and Table 5,5)
Power Circuit Breaker 3-Phase 230kV with CTs | Failure | Lognormal | 1 | 0.55 | 0.2 | -0.1 | 1 | 0 | NA | NA | NA | 21 | 4.26 | NA | NGCP judgement derived through consensus at Infrastructure Symposium with some validation to performance testing of CB by manufacturer.
Power Circuit Breaker 3-Phase 69kV with CTs | Failure | Lognormal | 1 | 0.85 | 0.3 | 0 | 1 | 0 | NA | NA | NA | 21 | 4.26 | NA | NGCP judgement derived through consensus at Infrastructure Symposium with some validation to performance testing of CB by manufacturer. Modified using med to low voltage adjustment made by FEMA (Syner-G Table 5.3 anchored of 0.3g at median and 0.05g at threshold)
Power Circuit Breaker 1-Phase 230kV | Failure | Lognormal | 1 | 0.55 | 0.2 | 0.03 | 1 | 0 | NA | NA | NA | 14 | 2.43 | NA | NGCP judgement derived through consensus at Infrastructure Symposium with some validation to performance testing of CB by manufacturer.
Power Transformer 100MVA 230/69 | Failure | Lognormal | 1 | 0.55 | 0.2 | NA | 0.3 | 0 | NA | NA | NA | 21 | 4.26 | NA | NGCP judgement derived through consensus at Infrastructure Symposium . Note that vulnerability is greater than that assessed by Anagnos (Syner-G Table 3.22)
Power Transformer 50MVA 230/69 | Failure | Lognormal | 1 | 0.55 | 0.2 | NA | 0.3 | 0 | NA | NA | NA | 21 | 3.04 | NA | NGCP judgement derived through consensus at Infrastrucutre Symposium . Note that vulnerability is greater than that assessed by Anagnos (Syner-G Table 3.22)
Power Transformer 20MVA 69/4.36 | Failure | Lognormal | 1 | 0.67 | 0.3 | -0.29 | 0.3 | 0 | NA | NA | NA | 21 | 1.82 | NA | NGCP judgement derived through concensus at Infrastructure Symposium shifted 0.12g to the right at median but no change at threshold to a lower vulnerability to reflect Syner G Table 5.11 presenting HAZUS functions.
Power Transformer 2.5MVA 69/4.16 | Failure | Lognormal | 1 | 0.67 | 0.3 | -0.29 | 0.3 | 0 | NA | NA | NA | 10 | 1.22 | NA | NGCP judgement derived through concensus at Infrastructure Symposium shifted 0.12g to the right at median but no change at threshold to a lower vulnerability to reflect Syner G Table 5.11 presenting HAZUS functions.
Control Building With Equipment BAK | Failure | Lognormal | 1 | 0.65 | 0.4 | -1.71 | 1 | 0 | NA | NA | NA | 75 | 9.12 | NA | RC Frame with masonry infill wall adapation of power house (0.3g assumed design level) at extensive damage state. Extensive damage state is assmed to be the severity at which the control equipment is rendered inoperable.
Control Building With Equipment | Failure | Lognormal | 1 | 0.86 | 0.38 | -1.71 | 1 | 0 | NA | NA | NA | 75 | 9.12 | NA | RC Frame with masonry infill wall adapation of power house (0.3g assumed design level) at extensive damage state. Extensive damage state is assmed to be the severity at which the control equipment is rendered inoperable.
Control Building With Equipment SDL0.4g | Failure | Lognormal | 1 | 0.86 | 0.38 | -1.71 | 1 | 0 | NA | NA | NA | 75 | 9.12 | NA | RC Frame with masonry infill wall adapation of power house (0.3g assumed design level) at extensive damage state. Extensive damage state is assmed to be the severity at which the control equipment is rendered inoperable.
Grounding | Failure | Lognormal | 1 | 1.08 | 0.54 | 0.08 | 0.95 | 0 | NA | NA | NA | 1 | 0.61 | NA | Assumed same as Lightning Arrester
Generation Source | Failure | Lognormal | 1 | 4 | 0.01 | 0.01 | 0.01 | 1 | NA | NA | NA | 1 | 0.01 | NA | Source. Unbreakable.
Bus 230kV | Failure | Lognormal | 1 | 99 | 0.01 | -0.37 | 0.95 | 0 | NA | NA | NA | 7 | 1.22 | NA | Assigned extremely high fragility as Bus is not modelled
Bus | Failure | Lognormal | 1 | 0.69 | 0.2 | -0.37 | 0.95 | 0 | NA | NA | NA | 7 | 1.22 | NA | Shinozuka, Dong, Chen, and Jin (2007)
SYSTEM_OUTPUT | Failure | Lognormal | 1 | 99 | 0.01 | 0.01 | 0.01 | 1 | NA | NA | NA | 1 | 0.01 | NA | Sink. Unbreakable.
CONN_NODE | Failure | Lognormal | 1 | 99 | 0.01 | 0.01 | 0.01 | 1 | NA | NA | NA | 1 | 0.01 | NA | Dummy node for interconnections.

## damage_state_def
component_type | damage_state | damage_state_definition | fragility_source
Capacitive Voltage Transformer 230kV | Failure | Porcelain cracking or overturning | Vanzi voltage transformer Syner-G Table 5.14
Capacitive Voltage Transformer 69kV | Failure | Porcelain cracking or overturning | Vanzi voltage transformer Syner-G Table 5.14
Current Transformer 230kV | Failure | Porcelain cracking or overturning | Median mid-way between Vanzi current and voltage transformer with damage threshold just below 0.4g
Disconnect Switch 230kV 3-Phase | Failure | Anchorage failure or overturning. | NGCP judgement derived through consensus at Infrastructure Symposium . Vulnerability corresponds closely with Vanzi horizontal disconnect (Syner-G Table 5.6).
Disconnect Switch 69kV 3-Phase | Failure | Anchorage failure or overturning. | NGCP judgement derived through consensus at Infrastructure Symposium . Vulnerability corresponds closely with Vanzi horizontal disconnect (Syner-G Table 5.6) but shifted proportionately as per MN HAZUS curves in Tbale 5.7 of Syner-G (0.36g at medium with no change at threshold).
Lightning Arrester | Failure | Anchorage failure or overturning. | Midway between Vanzi discharger and ligntning arrestor (Syner-G Table 5.4 and Table 5,5)
Power Circuit Breaker 3-Phase 230kV with CTs | Failure | Two porcelain column breakages with damage to anchorge | NGCP judgement derived through consensus at Infrastructure Symposium with some validation to performance testing of CB by manufacturer.
Power Circuit Breaker 3-Phase 69kV with CTs | Failure | Two porcelain column breakages with damage to anchorge | NGCP judgement derived through consensus at Infrastructure Symposium with some validation to performance testing of CB by manufacturer. Modified using med to low voltage adjustment made by FEMA (Syner-G Table 5.3 anchored of 0.3g at median and 0.05g at threshold)
Power Circuit Breaker 1-Phase 230kV | Failure | Two porcelain column breakages with damage to anchorge | NGCP judgement derived through consensus at Infrastructure Symposium with some validation to performance testing of CB by manufacturer.
Power Transformer 100MVA 230/69 | Failure | Gasket leakage to 2 or more bushings. One porcelain bushing breakage and major break in radiator | NGCP judgement derived through consensus at Infrastructure Symposium . Note that vulnerability is greater than that assessed by Anagnos (Syner-G Table 3.22)
Power Transformer 50MVA 230/69 | Failure | Gasket leakage to 2 or more bushings. One porcelain bushing breakage and major break in radiator | NGCP judgement derived through consensus at Infrastrucutre Symposium . Note that vulnerability is greater than that assessed by Anagnos (Syner-G Table 3.22)
Power Transformer 20MVA 69/4.36 | Failure | Gasket leakage to 2 or more bushings. One porcelain bushing breakage and major break in radiator | NGCP judgement derived through concensus at Infrastructure Symposium shifted 0.12g to the right at median but no change at threshold to a lower vulnerability to reflect Syner G Table 5.11 presenting HAZUS functions.
Power Transformer 2.5MVA 69/4.16 | Failure | Gasket leakage to 2 or more bushings. One porcelain bushing breakage and major break in radiator | NGCP judgement derived through concensus at Infrastructure Symposium shifted 0.12g to the right at median but no change at threshold to a lower vulnerability to reflect Syner G Table 5.11 presenting HAZUS functions.
Control Building With Equipment | Failure | Most infill walls exhibit large cracks. Some bricks may dislodge and fall. Some walls may bulge out-of-plane. A few walls may fall partially or fully. A few concrete columns or beams may fail in shear resulting in partial collapse. Structure may exhibit permanent lateral deformation. Most partitions are cracked and many need replacement. Ceiling “T” bar system exhibits extensive buckling and with many light fittings fall. Extensive damage to exterior wall panels and most connections require inspection. | RC Frame with masonry infill wall adapation of power house (0.3g assumed design level) at extensive damage state. Extensive damage state is assmed to be the severity at which the control equipment is rendered inoperable.
Grounding | Failure | not available | Assumed same as Lightning Arrester
Generation Source | Failure | not available | Source. Unbreakable.
Bus 230kV | Failure | not available | Shinozuka, Dong, Chen, and Jin (2007)
SYSTEM_OUTPUT | Failure | not available | Sink. Unbreakable.
CONN_NODE | Failure | not available | Dummy node for interconnections.

## comptype_costs_230kv
Description: | Cost of the system components
Note:
component_type | # Assets | Cost per Unit | Aggregate cost for component type | Fractional Cost (aggregated by component type) | Fractional Cost (for each component type) | Recovery/Replacement Time (Mean) | Recovery/Replacement Time (Likely Variation - Standard Dev)
Capacitive Voltage Transformer 230kV | 16 | 8000 | 128000 | 0.014987 | 0.00093667
Current Transformer 230kV | 38 | 11000 | 418000 | 0.048941 | 0.0012879
Disconnect Switch 230kV 3-Phase | 51 | 11900 | 606900 | 0.071058 | 0.0013933
Lightning Arrester | 10 | 3000 | 30000 | 0.0035125 | 0.00035125
Power Circuit Breaker 3-Phase 230kV with CTs | 12 | 124000 | 1488000 | 0.17422 | 0.014518
Power Circuit Breaker 1-Phase 230kV | 21 | 60000 | 1260000 | 0.14753 | 0.007025
Power Transformer 100MVA 230/69 | 1 | 1290000 | 1290000 | 0.15104 | 0.15104
Power Transformer 50MVA 230/69 | 1 | 1120000 | 1120000 | 0.13113 | 0.13113
Control Building With Equipment | 1 | 2200000 | 2200000 | 0.25758 | 0.25758
Bus | 3 | 0 | 0 | 0 | 0
Other components (not accounted here)
TOTAL |  | 4827900 | 8540900 | 1

## comptype_costs_all
Description: | Cost of the system components
Note:
component_type | # Assets | Cost per Unit | Aggregate cost for component type | Fractional Cost (aggregated by component type) | Fractional Cost (for each component type) | Recovery/Replacement Time (Mean) | Recovery/Replacement Time (Likely Variation - Standard Dev)
Capacitive Voltage Transformer 230kV | 16 | 8000 | 128000 | 0.013732 | 0.00085824
Capacitive Voltage Transformer 69kV | 15 | 5200 | 78000 | 0.0083678 | 0.00055786
Current Transformer 230kV | 38 | 11000 | 418000 | 0.044843 | 0.0011801
Disconnect Switch 230kV 3-Phase | 51 | 11900 | 606900 | 0.065108 | 0.0012766
Disconnect Switch 69kV 3-Phase | 10 | 7700 | 77000 | 0.0082606 | 0.00082606
Lightning Arrester | 14 | 3000 | 42000 | 0.0045058 | 0.00032184
Power Circuit Breaker 3-Phase 230kV with CTs | 12 | 124000 | 1488000 | 0.15963 | 0.013303
Power Circuit Breaker 3-Phase 69kV with CTs | 6 | 46000 | 276000 | 0.029609 | 0.0049349
Power Circuit Breaker 1-Phase 230kV | 21 | 60000 | 1260000 | 0.13517 | 0.0064368
Power Transformer 100MVA 230/69 | 1 | 1290000 | 1290000 | 0.13839 | 0.13839
Power Transformer 50MVA 230/69 | 1 | 1120000 | 1120000 | 0.12015 | 0.12015
Power Transformer 20MVA 69/4.36 | 1 | 300000 | 300000 | 0.032184 | 0.032184
Power Transformer 2.5MVA 69/4.16 | 1 | 37500 | 37500 | 0.004023 | 0.004023
Control Building With Equipment | 1 | 2200000 | 2200000 | 0.23602 | 0.23602
Bus | 3 | 0 | 0 | 0 | 0
Other components (not accounted here)
TOTAL |  | 5224300 | 9321400 | 1