## system_meta
model_config_param | value | notes
infrastructure_level | facility
system_class | PotableWaterTreatmentPlant
system_subclass | Small Water Treatment Plant | Capacity is 165 ML/d (43.5 MG/d) expandable to 240 ML/d (63.4 MG/d). With its current capacity it is considered to be a small treatment plant, according to HAZUS clasification.
component_location_conf | defined
restoration_time_unit | days

## table_description
Table Name | Description | Note
component_list | This file lists the instances of various component types within the system. Component design level x.xx g. | Cost fractions define economic value of the individual component relative to the cost of entire system. Data includes a __% allowance for components not included in the model.
component_connections | Network connections. Each pair of nodes implies a connecting edge. Directionality is defined by order of nodes in a row (Orig -> Dest). | Used by: (1) network algorithm package for flow calculations, (2) Pygraphviz to draw the system layout.
supply_setup | Necessary input materiél required for plant operation. | Capacity given as percentage.
output_setup | Treatment Capacity in Mega Litres per Day (MLD)
comp_type_dmg_algo | List of component types with fragility and recovery data | Fragilities are defined according to discrete damage states. Recovery time is in DAYS.
damage_state_def | Definitions of damage states of the list of component types in the system

## component_list
component_id | component_type | component_class | cost_fraction | node_type | node_cluster | operating_capacity | pos_x | pos_y
Backup_Genset_Transformer | Transformer | Backup Power | 0.04 | transshipment | ZONE 6A | 1 | 200 | 250
Bldg_Blower_Compression | Building 0.15g | Building | 0.005 | dependency | ZONE 2 | 1 | 20 | 1710
Bldg_Chem_N1 | Building 0.15g | Building | 0.005 | dependency | ZONE 2 | 1 | 20 | 1500
Bldg_UV_Dosing | UV Dosing Equipment | Building | 0.03 | transshipment | ZONE 4A | 1 | 620 | 1065
Bldg_Cl | Chlorination Equipment | Building | 0.03 | dependency | ZONE 4B | 1 | 780 | 895
Bldg_Chem_N2 | Chemical Building | Building | 0.005 | dependency | ZONE 5 | 1 | 985 | 735
Bldg_Clearwater_PumpStn | Building 0.15g | Building | 0.02 | dependency | ZONE 6A | 1 | 300 | 570
Chem_Tank_ALUM_No1 | Chemical Tank - ALUM | Chemical Tank | 0.007 | transshipment | ZONE 2 | 1 | 260 | 1430
Chem_Tank_ALUM_No2 | Chemical Tank - ALUM | Chemical Tank | 0.007 | transshipment | ZONE 2 | 1 | 260 | 1490
Chem_Tank_NaOH_No1 | Chemical Tank - NaOH | Chemical Tank | 0.007 | transshipment | ZONE 5 | 1 | 940 | 649
Chem_Tank_NaOH_No2 | Chemical Tank - NaOH | Chemical Tank | 0.007 | transshipment | ZONE 5 | 1 | 940 | 589
Chem_Tank_FSA_No1 | Chemical Tank - FSA | Chemical Tank | 0.007 | transshipment | ZONE 5 | 1 | 1030 | 649
Chem_Tank_FSA_No2 | Chemical Tank - FSA | Chemical Tank | 0.007 | transshipment | ZONE 5 | 1 | 1030 | 589
Contact_Tank_Cl | Concrete Tank 20x20 CLCONTACT | Chlorination Tank | 0.04 | transshipment | ZONE 4B | 1 | 620 | 900
Switchroom_HV | Switchrooms | Commercial Power | 0.02 | transshipment | ZONE 6B | 1 | 660 | 230
Chem_Dosing_Panel_ALUM | Chemical Dosing Panel | Electrical Equipment | 0.005 | transshipment | ZONE 2 | 1 | 320 | 1390
Switchroom_LV_Xfmr_N1 | Switchrooms | Electrical Equipment | 0.015 | transshipment | ZONE 3 | 1 | 1070 | 1300
Switchroom_LV_Xfmr_N2 | Switchrooms | Electrical Equipment | 0.015 | transshipment | ZONE 4A | 1 | 460 | 1135
Switchroom_HV-LV | Switchrooms | Electrical Equipment | 0.02 | transshipment | ZONE 6B | 1 | 400 | 230
Xfmr_HV-LV | Transformer Dry Type | Electrical Equipment | 0.02 | transshipment | ZONE 6B | 1 | 530 | 230
Chem_Dosing_Panel_NaOH | Chemical Dosing Panel | Equipment | 0.015 | transshipment | ZONE 5 | 1 | 940 | 525
Chem_Dosing_Panel_FSA | Chemical Dosing Panel | Equipment | 0.015 | transshipment | ZONE 5 | 1 | 1030 | 525
Clearwater_Pump_Control_Panels | Switchrooms | Equipment | 0.015 | transshipment | ZONE 6B | 1 | 400 | 355
Tank_Diesel_Storage | Diesel Storage Tank Horizontal | Fuel Storage Tank | 0.015 | supply | ZONE 6B | 1 | 200 | 110
Backup_Genset | Genset 3100kVA | Generator | 0.015 | transshipment | ZONE 6A | 1 | 200 | 185
Power_Supply_Commercial | SYSTEM_INPUT | MODEL ARTEFACT | 0 | supply | ZONE 6B | 1 | 660 | 100
Water_Supply | SYSTEM_INPUT | MODEL ARTEFACT | 0 | supply | ZONE 7 | 1 | 1180 | 100
Saturated_Air_Supply | JUNCTION | MODEL ARTEFACT | 0 | junction | ZONE 1 | 1 | 340 | 1580
Power_Supply_Area_3 | JUNCTION | MODEL ARTEFACT | 0 | junction | ZONE 2 | 1 | 950 | 1300
Power_Supply_Area_2 | JUNCTION | MODEL ARTEFACT | 0 | junction | ZONE 4A | 1 | 460 | 1060
Output_Freshwater | SYSTEM_OUTPUT | MODEL ARTEFACT | 0 | sink | ZONE 7 | 1 | 820 | 100
Power_Supply_Main | JUNCTION | MODEL ARTEFACT | 0 | junction | ZONE 6A | 1 | 50 | 300
Power_Supply_Area_1 | JUNCTION | MODEL ARTEFACT | 0 | junction | ZONE 6A | 1 | 530 | 320
Pipe_Main_Inlet_Section_1 | Pipe Main Inlet | Pipework | 0.002 | transshipment | ZONE 7 | 1 | 1180 | 405
Pipe_Main_Inlet_Tee_Connector | Elevated Pipework | Pipework | 0.002 | transshipment | ZONE 5 | 1 | 1180 | 1165
Pipe_Main_Inlet_to_FLOC | Elevated Pipework | Pipework | 0.002 | transshipment | ZONE 0 | 1 | 540 | 1735
Pipe_Main_Inlet_to_UV | Elevated Pipework | Pipework | 0.002 | transshipment | ZONE 4A | 1 | 640 | 1165
Pipe_FLOC_DAFF_Connector | Elevated Pipework | Pipework | 0.002 | transshipment | ZONE 1 CONN-IN | 1 | 540 | 1545
Pipe_DAFF_to_BAC | Pipe Connector Buried | Pipework | 0.002 | transshipment | ZONE 2 CONN-IN | 1 | 540 | 1390
Pipe_BAC_to_BALANCETANK | Elevated Pipework | Pipework | 0.002 | transshipment | ZONE 4 CONN-IN | 1 | 540 | 1230
Pipe_Cl_Contact_to_Clearwater | Pipe Section DN1400 | Pipework | 0.002 | transshipment | ZONE 5 CONN-IN | 1 | 620 | 835
Pipe_Clearwater_Inlet_Joint | Pipe Section DN1400 | Pipework | 0.002 | transshipment | ZONE 5 CONN-IN | 1 | 620 | 795
Pipe_Clearwater1_Pumphouse | Pipe Section DN1400 | Pipework | 0.002 | transshipment | ZONE 5 CONN-IN | 1 | 480 | 645
Pipe_Clearwater2_Pumphouse | Pipe Section DN1400 | Pipework | 0.002 | transshipment | ZONE 5 CONN-IN | 1 | 620 | 645
Pumphouse_Inlet_Joint | Pipe Section DN1700 | Pipework | 0.002 | transshipment | ZONE 5 CONN-IN | 1 | 550 | 585
Clearwater_Pump_Output_Connector | Elevated Pipework | Pipework | 0.002 | transshipment | ZONE 6A | 1 | 750 | 390
Pipe_Main_Outlet | Pipe Section DN1200 | Pipework | 0.002 | transshipment | ZONE 6A | 1 | 820 | 270
Backwash_Pumps | Pump Backwash | Pump | 0.01 | transshipment | ZONE 3 | 1 | 860 | 1300
Supernatant_Pumps_Filter_UV_Dosing | Pump Backwash | Pump | 0.01 | transshipment | ZONE 5 | 1 | 250 | 735
Clearwater_Pump_N1 | Pump Horizontal 1600kW | Pump | 0.025 | transshipment | ZONE 6A | 1 | 400 | 475
Clearwater_Pump_N2 | Pump Horizontal 1600kW | Pump | 0.025 | transshipment | ZONE 6A | 1 | 500 | 475
Clearwater_Pump_N3 | Pump Horizontal 1600kW | Pump | 0.025 | transshipment | ZONE 6A | 1 | 600 | 475
Clearwater_Pump_N4 | Pump Horizontal 1600kW | Pump | 0.025 | transshipment | ZONE 6A | 1 | 700 | 475
DAFF_Tanks | Concrete Tank 30x70 DAFF | Sedimentation Basin - Large | 0.08 | transshipment | ZONE 2 | 1 | 540 | 1460
BAC_Filters | Concrete Tank 20x80 BACFILTER | Sedimentation Basin - Large | 0.08 | transshipment | ZONE 3 | 1 | 540 | 1300
FLOC_Tanks | Concrete Tank 20x25 FLOC | Sedimentation Basin - Small | 0.06 | transshipment | ZONE 1 | 1 | 540 | 1635
Tank_Backwash_Water | Concrete Tank 20x20 BKWSH | Small Tank | 0.03 | transshipment | ZONE 3 | 1 | 730 | 1300
Tank_Balancing | Concrete Tank BALANCING | Small Tank | 0.03 | transshipment | ZONE 4A | 1 | 620 | 985
Tank_BAC_Rinse_Supernatant | Concrete Tank 10X20 BACRINSE | Small Tank | 0.03 | transshipment | ZONE 5 | 1 | 340 | 735
Tank_Clearwater_N1 | Concrete Tank 30x30 CLRWTR | Small Tank | 0.05 | transshipment | ZONE 5 | 1 | 480 | 735
Tank_Clearwater_N2 | Concrete Tank 30x30 CLRWTR | Small Tank | 0.05 | transshipment | ZONE 5 | 1 | 620 | 735
Air_Receiver_1 | Air Tank Vertical | Steel Tank | 0.0025 | transshipment | ZONE 1 | 1 | 180 | 1580
Air_Receiver_2 | Air Tank Vertical | Steel Tank | 0.0025 | transshipment | ZONE 1 | 1 | 180 | 1630
Compressed_Air_Vessel_1 | Compressed Air Vessel | Steel Tank | 0.003 | transshipment | ZONE 1 | 1 | 180 | 1680
Compressed_Air_Vessel_2 | Compressed Air Vessel | Steel Tank | 0.003 | transshipment | ZONE 1 | 1 | 180 | 1730
Compressed_Air_Vessel_3 | Compressed Air Vessel | Steel Tank | 0.003 | transshipment | ZONE 1 | 1 | 180 | 1780
Compressed_Air_Vessel_4 | Compressed Air Vessel | Steel Tank | 0.003 | transshipment | ZONE 1 | 1 | 180 | 1830
Tank_CO2_Storage | Steel Tank Liquid CO2 | Steel Tank | 0.005 | dependency | ZONE 5 | 1 | 845 | 615
Surge_Vessels | Surge Vessels | Surge Vessels | 0.015 | transshipment | ZONE 6A | 1 | 820 | 450

## component_connections
origin | destination | link_capacity | weight
Power_Supply_Commercial | Switchroom_HV | 1 | 1
Switchroom_HV | Power_Supply_Main | 1 | 1
Tank_Diesel_Storage | Backup_Genset | 1 | 1
Backup_Genset | Switchroom_HV-LV | 1 | 1
Switchroom_HV-LV | Backup_Genset_Transformer | 1 | 1
Backup_Genset_Transformer | Power_Supply_Main | 1 | 1
Xfmr_HV-LV | Switchroom_HV-LV | 1 | 1
Power_Supply_Main | Xfmr_HV-LV | 1 | 1
Power_Supply_Main | Switchroom_LV_Xfmr_N2 | 1 | 1
Power_Supply_Main | Switchroom_LV_Xfmr_N1 | 1 | 1
Xfmr_HV-LV | Power_Supply_Area_1 | 1 | 1
Switchroom_LV_Xfmr_N2 | Power_Supply_Area_2 | 1 | 1
Switchroom_LV_Xfmr_N1 | Power_Supply_Area_3 | 1 | 1
Power_Supply_Area_3 | Bldg_Chem_N1 | 1 | 1
Power_Supply_Area_3 | Chem_Dosing_Panel_ALUM | 1 | 1
Power_Supply_Area_3 | FLOC_Tanks | 1 | 1
Power_Supply_Area_3 | DAFF_Tanks | 1 | 1
Power_Supply_Area_3 | BAC_Filters | 1 | 1
Power_Supply_Area_3 | Backwash_Pumps | 1 | 1
Power_Supply_Area_2 | Bldg_UV_Dosing | 1 | 1
Power_Supply_Area_2 | Contact_Tank_Cl | 1 | 1
Power_Supply_Area_2 | Chem_Dosing_Panel_FSA | 1 | 1
Power_Supply_Area_2 | Chem_Dosing_Panel_NaOH | 1 | 1
Power_Supply_Area_2 | Supernatant_Pumps_Filter_UV_Dosing | 1 | 1 | >> purpose: feed wash water back to water entry point; source of power: AREA 2
Supernatant_Pumps_Filter_UV_Dosing | Tank_BAC_Rinse_Supernatant | 1 | 1
Water_Supply | Pipe_Main_Inlet_Section_1 | 1 | 1
Pipe_Main_Inlet_Section_1 | Pipe_Main_Inlet_Tee_Connector | 1 | 1
Pipe_Main_Inlet_Tee_Connector | Pipe_Main_Inlet_to_FLOC | 1 | 1
Pipe_Main_Inlet_to_FLOC | FLOC_Tanks | 1 | 1
FLOC_Tanks | Pipe_FLOC_DAFF_Connector | 1 | 1
Pipe_FLOC_DAFF_Connector | DAFF_Tanks | 1 | 1
Bldg_Blower_Compression | Air_Receiver_1 | 1 | 1
Bldg_Blower_Compression | Air_Receiver_2 | 1 | 1
Bldg_Blower_Compression | Compressed_Air_Vessel_1 | 2 | 1
Bldg_Blower_Compression | Compressed_Air_Vessel_2 | 2 | 1
Bldg_Blower_Compression | Compressed_Air_Vessel_3 | 2 | 1
Bldg_Blower_Compression | Compressed_Air_Vessel_4 | 2 | 1
Air_Receiver_1 | Saturated_Air_Supply | 1 | 1
Air_Receiver_2 | Saturated_Air_Supply | 1 | 1
Compressed_Air_Vessel_1 | Saturated_Air_Supply | 2 | 1
Compressed_Air_Vessel_2 | Saturated_Air_Supply | 2 | 1
Compressed_Air_Vessel_3 | Saturated_Air_Supply | 2 | 1
Compressed_Air_Vessel_4 | Saturated_Air_Supply | 2 | 1
Bldg_Chem_N1 | Chem_Tank_ALUM_No1 | 1 | 1
Bldg_Chem_N1 | Chem_Tank_ALUM_No2 | 1 | 1
Chem_Dosing_Panel_ALUM | Chem_Tank_ALUM_No1 | 1 | 1
Chem_Dosing_Panel_ALUM | Chem_Tank_ALUM_No2 | 1 | 1
Saturated_Air_Supply | DAFF_Tanks | 1 | 1
Chem_Tank_ALUM_No1 | DAFF_Tanks | 1 | 1 | >> alum for DAFF
Chem_Tank_ALUM_No2 | DAFF_Tanks | 1 | 1
DAFF_Tanks | Pipe_DAFF_to_BAC | 1 | 1
Pipe_DAFF_to_BAC | BAC_Filters | 1 | 1
Backwash_Pumps | Tank_Backwash_Water | 1 | 1
Tank_Backwash_Water | BAC_Filters | 1 | 1
BAC_Filters | Pipe_BAC_to_BALANCETANK | 1 | 1
Pipe_BAC_to_BALANCETANK | Tank_Balancing | 1 | 1 | >> purpose of balance tank
Tank_Balancing | Contact_Tank_Cl | 1 | 1
Pipe_Main_Inlet_Tee_Connector | Pipe_Main_Inlet_to_UV | 1 | 1
Pipe_Main_Inlet_to_UV | Bldg_UV_Dosing | 1 | 1
Bldg_UV_Dosing | Tank_Balancing | 1 | 1
Bldg_Cl | Contact_Tank_Cl | 1 | 1
Contact_Tank_Cl | Pipe_Cl_Contact_to_Clearwater | 1 | 1
Pipe_Cl_Contact_to_Clearwater | Pipe_Clearwater_Inlet_Joint | 1 | 1
Pipe_Clearwater_Inlet_Joint | Tank_Clearwater_N1 | 1 | 1
Pipe_Clearwater_Inlet_Joint | Tank_Clearwater_N2 | 1 | 1
Bldg_Chem_N2 | Chem_Dosing_Panel_NaOH | 1 | 1
Bldg_Chem_N2 | Chem_Dosing_Panel_FSA | 1 | 1
Bldg_Chem_N2 | Chem_Tank_NaOH_No1 | 1 | 1
Bldg_Chem_N2 | Chem_Tank_NaOH_No2 | 1 | 1
Bldg_Chem_N2 | Chem_Tank_FSA_No1 | 1 | 1
Bldg_Chem_N2 | Chem_Tank_FSA_No2 | 1 | 1
Chem_Dosing_Panel_NaOH | Chem_Tank_NaOH_No1 | 1 | 1 | >> why does NaOH dosing happen: to adjust the pH up, connects to the exit pipe out of the Contact Tank
Chem_Dosing_Panel_NaOH | Chem_Tank_NaOH_No2 | 1 | 1
Chem_Dosing_Panel_FSA | Chem_Tank_FSA_No1 | 1 | 1 | >> why does FSA dosing happen: to add Fl to water, connects to the exit pipe out of the Contact Tank
Chem_Dosing_Panel_FSA | Chem_Tank_FSA_No2 | 1 | 1
Chem_Tank_NaOH_No1 | Pumphouse_Inlet_Joint | 1 | 1
Chem_Tank_NaOH_No2 | Pumphouse_Inlet_Joint | 1 | 1
Chem_Tank_FSA_No1 | Pumphouse_Inlet_Joint | 1 | 1
Chem_Tank_FSA_No2 | Pumphouse_Inlet_Joint | 1 | 1
Tank_CO2_Storage | Tank_Clearwater_N1 | 1 | 1 | >> why does CO2 dosing happen: to adjust the pH down, connects to the exit pipe out of the Contact Tank
Tank_CO2_Storage | Tank_Clearwater_N2 | 1 | 1
Power_Supply_Area_1 | Clearwater_Pump_Control_Panels | 1 | 1
Tank_Clearwater_N1 | Pipe_Clearwater1_Pumphouse | 1 | 1
Tank_Clearwater_N2 | Pipe_Clearwater2_Pumphouse | 1 | 1
Pipe_Clearwater1_Pumphouse | Pumphouse_Inlet_Joint | 1 | 1
Pipe_Clearwater2_Pumphouse | Pumphouse_Inlet_Joint | 1 | 1
Pumphouse_Inlet_Joint | Clearwater_Pump_N1 | 1 | 1
Pumphouse_Inlet_Joint | Clearwater_Pump_N2 | 1 | 1
Pumphouse_Inlet_Joint | Clearwater_Pump_N3 | 1 | 1
Pumphouse_Inlet_Joint | Clearwater_Pump_N4 | 1 | 1
Bldg_Clearwater_PumpStn | Clearwater_Pump_N1 | 1 | 1
Bldg_Clearwater_PumpStn | Clearwater_Pump_N2 | 1 | 1
Bldg_Clearwater_PumpStn | Clearwater_Pump_N3 | 1 | 1
Bldg_Clearwater_PumpStn | Clearwater_Pump_N4 | 1 | 1
Clearwater_Pump_Control_Panels | Clearwater_Pump_N1 | 1 | 1
Clearwater_Pump_Control_Panels | Clearwater_Pump_N2 | 1 | 1
Clearwater_Pump_Control_Panels | Clearwater_Pump_N3 | 1 | 1
Clearwater_Pump_Control_Panels | Clearwater_Pump_N4 | 1 | 1
Clearwater_Pump_N1 | Clearwater_Pump_Output_Connector | 1 | 1
Clearwater_Pump_N2 | Clearwater_Pump_Output_Connector | 1 | 1
Clearwater_Pump_N3 | Clearwater_Pump_Output_Connector | 1 | 1
Clearwater_Pump_N4 | Clearwater_Pump_Output_Connector | 1 | 1
Clearwater_Pump_Output_Connector | Surge_Vessels | 1 | 1
Power_Supply_Area_1 | Surge_Vessels | 1 | 1
Surge_Vessels | Pipe_Main_Outlet | 1 | 1 | >> how and where does it link to output pipes
Pipe_Main_Outlet | Output_Freshwater | 1 | 1

## supply_setup
input_node | input_capacity | capacity_fraction | commodity_type
Water_Supply | 100 | 1 | Untreated Water
Power_Supply_Commercial | 100 | 1 | Electric Power

## output_setup
output_node | production_node | output_node_capacity | capacity_fraction | priority
Output_Freshwater | pipe_to_distro_1 | 165 | 1 | 1

## comp_type_dmg_algo
id | component_type | damage_state | is_piecewise | damage_function | median | location | beta | minimum | lower_limit | upper_limit | damage_ratio | functionality | recovery_function | recovery_mean | recovery_std | recovery_95percentile | fragility_source | notes
1 | Pump Horizontal - HAZUS-A | DS1 Slight | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0 | 0.95 | Normal | 5 | 0.30398 | 0.5 | HAZUS algorithm for `Horizontal Pump - Anchored - Pumping Plant Subcomponent`. NIBS 2003, Table A.8.1, Table 15B.5.
2 | Pump Horizontal - HAZUS-A | DS2 Moderate | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0 | 0.75 | Normal | 17 | 0.60796 | 1
3 | Pump Horizontal - HAZUS-A | DS3 Extensive | no | Lognormal | 1.6 | 0 | 0.6 | NA | null | null | 0.75 | 0.3 | Normal | 37 | 1.2159 | 2
4 | Pump Horizontal - HAZUS-A | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0 | 0 | Normal | 77.1429 | 2.4318 | 4
5 | Pump Vertical - HAZUS-A | DS1 Slight | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0 | 0.95 | Normal | 5 | 0.30398 | 0.5 | HAZUS algorithm for `Vertical Pump - Anchored - Pumping Plant Subcomponent`. NIBS 2003, Table A.8.1, Table 15B.5.
6 | Pump Vertical - HAZUS-A | DS2 Moderate | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0 | 0.75 | Normal | 17 | 0.60796 | 1
7 | Pump Vertical - HAZUS-A | DS3 Extensive | no | Lognormal | 1.25 | 0 | 0.6 | NA | null | null | 0.75 | 0.3 | Normal | 37 | 1.2159 | 2
8 | Pump Vertical - HAZUS-A | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 1 | 0 | Normal | 77.1429 | 2.4318 | 4
9 | SYSTEM_INPUT | DS1 Slight | no | Lognormal | 99 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 5 | 0.30398 | 0.5 | Assigned unbreakable fragiity. | This component is a necessary artefact of of the model.
10 | SYSTEM_INPUT | DS2 Moderate | no | Lognormal | 99 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 17 | 0.60796 | 1
11 | SYSTEM_INPUT | DS3 Extensive | no | Lognormal | 99 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 37 | 1.2159 | 2
12 | SYSTEM_INPUT | DS4 Complete | no | Lognormal | 99 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 77.1429 | 2.4318 | 4
13 | SYSTEM_OUTPUT | DS1 Slight | no | Lognormal | 99 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 5 | 0.30398 | 0.5 | Assigned unbreakable fragiity. | This component is a necessary artefact of of the model.
14 | SYSTEM_OUTPUT | DS2 Moderate | no | Lognormal | 99 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 17 | 0.60796 | 1
15 | SYSTEM_OUTPUT | DS3 Extensive | no | Lognormal | 99 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 37 | 1.2159 | 2
16 | SYSTEM_OUTPUT | DS4 Complete | no | Lognormal | 99 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 77.1429 | 2.4318 | 4
17 | JUNCTION | DS1 Slight | no | Lognormal | 99 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 5 | 0.30398 | 0.5 | Assigned unbreakable fragiity. | This component is a necessary artefact of of the model.
18 | JUNCTION | DS2 Moderate | no | Lognormal | 9 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 17 | 0.60796 | 1
19 | JUNCTION | DS3 Extensive | no | Lognormal | 99 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 37 | 1.2159 | 2
20 | JUNCTION | DS4 Complete | no | Lognormal | 99 | 0 | 1 | NA | null | null | 0 | 1 | Normal | 77.1429 | 2.4318 | 4
21 | Electric Power Commercial | DS1 Slight | no | Lognormal | 0.15 | 0 | 0.4 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | Based on HAZUS Unanchored Switchroom. Building 1.5g for Extensive and Complete.
22 | Electric Power Commercial | DS2 Moderate | no | Lognormal | 0.3 | 0 | 0.4 | NA | null | null | 0.4 | 0.75 | Normal | 20 | 1.2159 | 2
23 | Electric Power Commercial | DS3 Extensive | no | Lognormal | 0.55 | 0 | 0.4 | NA | null | null | 0.75 | 0.3 | Normal | 60 | 2.4318 | 4
24 | Electric Power Commercial | DS4 Complete | no | Lognormal | 0.8 | 0 | 0.4 | NA | null | null | 0.9 | 0 | Normal | 102.8571 | 4.8637 | 8
25 | Switchrooms | DS1 Slight | no | Lognormal | 0.15 | 0 | 0.4 | NA | null | null | 0.2 | 0.95 | Normal | 1 | 0.30398 | 0.5 | GA adaptation. HAZUS Unanchored algorithm for swtichrooms. Building 0.15 for Extensive and Complete.
26 | Switchrooms | DS2 Moderate | no | Lognormal | 0.3 | 0 | 0.4 | NA | null | null | 0.5 | 0.75 | Normal | 4 | 0.60796 | 1
27 | Switchrooms | DS3 Extensive | no | Lognormal | 0.55 | 0 | 0.4 | NA | null | null | 0.8 | 0.3 | Normal | 8 | 1.2159 | 2
28 | Switchrooms | DS4 Complete | no | Lognormal | 0.8 | 0 | 0.4 | NA | null | null | 1 | 0 | Normal | 12 | 2.4318 | 4
29 | Air Tank Vertical | DS1 Slight | no | Lognormal | 0.2 | 0 | 0.5 | NA | null | null | 0.1 | 0.95 | Normal | 2 | 0.60796 | 1 | Expert Judgment
30 | Air Tank Vertical | DS2 Moderate | no | Lognormal | 0.25 | 0 | 0.5 | NA | null | null | 0.4 | 0.75 | Normal | 5 | 1.2159 | 2 | Expert Judgment
31 | Air Tank Vertical | DS3 Extensive | no | Lognormal | 0.3 | 0 | 0.5 | NA | null | null | 0.7 | 0.3 | Normal | 14 | 2.4318 | 4 | Expert Judgment
32 | Air Tank Vertical | DS4 Complete | no | Lognormal | 0.5 | 0 | 0.5 | NA | null | null | 0.99 | 0 | Normal | 28 | 4.8637 | 8 | Expert Judgment
33 | Building 0.15g | DS1 Slight | no | Lognormal | 0.23 | 0 | 0.25 | NA | null | null | 0.1 | 0.95 | Normal | 5 | 0.60796 | 1 | Algorithm based on fragility for Philippines Power House, adjusted to 0.15g
34 | Building 0.15g | DS2 Moderate | no | Lognormal | 0.38 | 0 | 0.35 | NA | null | null | 0.4 | 0.75 | Normal | 20 | 1.2159 | 2
35 | Building 0.15g | DS3 Extensive | no | Lognormal | 0.55 | 0 | 0.4 | NA | null | null | 0.8 | 0.3 | Normal | 50 | 2.4318 | 4
36 | Building 0.15g | DS4 Complete | no | Lognormal | 0.8 | 0 | 0.4 | NA | null | null | 1 | 0 | Normal | 102.8571 | 4.8637 | 8
37 | Chemical Building | DS1 Slight | no | Lognormal | 0.23 | 0 | 0.25 | NA | null | null | 0.1 | 0.95 | Normal | 5 | 0.60796 | 1 | Assigned fragility of algorithm for: `Building 0.15g`
38 | Chemical Building | DS2 Moderate | no | Lognormal | 0.38 | 0 | 0.35 | NA | null | null | 0.4 | 0.75 | Normal | 20 | 1.2159 | 2
39 | Chemical Building | DS3 Extensive | no | Lognormal | 0.55 | 0 | 0.4 | NA | null | null | 0.8 | 0.3 | Normal | 50 | 2.4318 | 4
40 | Chemical Building | DS4 Complete | no | Lognormal | 0.8 | 0 | 0.4 | NA | null | null | 1 | 0 | Normal | 102.8571 | 4.8637 | 8
41 | Chemical Dosing Panel | DS1 Slight | no | Lognormal | 0.15 | 0 | 0.5 | NA | null | null | 0.1 | 0.95 | Normal | 5 | 0.60796 | 1 | Based on HAZUS curves for `Chlorination Equipment`. | Shifted to the right and steepened due to poor base fixity. Moderate damage much less likely.
42 | Chemical Dosing Panel | DS2 Moderate | no | Lognormal | 0.7 | 0 | 0.7 | NA | null | null | 0.4 | 0.75 | Normal | 20 | 1.2159 | 2
43 | Chemical Dosing Panel | DS3 Extensive | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.8 | 0.3 | Normal | 50 | 2.4318 | 4
44 | Chemical Dosing Panel | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 1 | 0 | Normal | 102.8571 | 4.8637 | 8
45 | Chemical Tanks | DS1 Slight | no | Lognormal | 0.13 | 0 | 0.5 | NA | null | null | 0.2 | 0.95 | Normal | 5 | 0.30398 | 0.5 | GA adaptation of HAZUS algorithm for `Steel Tank Above Ground`. | Median shift 0.05 OA. Moderate 0.2g additional shift. Extensive and Complete 0.4g additional shift left.
46 | Chemical Tanks | DS2 Moderate | no | Lognormal | 0.3 | 0 | 0.5 | NA | null | null | 0.75 | 0.75 | Normal | 17 | 0.60796 | 1
47 | Chemical Tanks | DS3 Extensive | no | Lognormal | 0.5 | 0 | 0.6 | NA | null | null | 0.85 | 0.3 | Normal | 37 | 1.2159 | 2
48 | Chemical Tanks | DS4 Complete | no | Lognormal | 1.05 | 0 | 0.6 | NA | null | null | 0.9 | 0 | Normal | 77.1429 | 2.4318 | 4
49 | Chemical Tank - ALUM | DS1 Slight | no | Lognormal | 0.13 | 0 | 0.5 | NA | null | null | 0.1 | 0.95 | Normal | 5 | 0.60796 | 1 | Assigned fragility of algorithm for: `Chemical Tanks`
50 | Chemical Tank - ALUM | DS2 Moderate | no | Lognormal | 0.3 | 0 | 0.5 | NA | null | null | 0.4 | 0.75 | Normal | 20 | 1.2159 | 2
51 | Chemical Tank - ALUM | DS3 Extensive | no | Lognormal | 0.5 | 0 | 0.6 | NA | null | null | 0.8 | 0.3 | Normal | 50 | 2.4318 | 4
52 | Chemical Tank - ALUM | DS4 Complete | no | Lognormal | 1.05 | 0 | 0.6 | NA | null | null | 1 | 0 | Normal | 102.8571 | 4.8637 | 8
53 | Chemical Tank - FSA | DS1 Slight | no | Lognormal | 0.13 | 0 | 0.5 | NA | null | null | 0.1 | 0.95 | Normal | 5 | 0.60796 | 1 | Assigned fragility of algorithm for: `Chemical Tanks`
54 | Chemical Tank - FSA | DS2 Moderate | no | Lognormal | 0.3 | 0 | 0.5 | NA | null | null | 0.4 | 0.75 | Normal | 20 | 1.2159 | 2
55 | Chemical Tank - FSA | DS3 Extensive | no | Lognormal | 0.5 | 0 | 0.6 | NA | null | null | 0.8 | 0.3 | Normal | 50 | 2.4318 | 4
56 | Chemical Tank - FSA | DS4 Complete | no | Lognormal | 1.05 | 0 | 0.6 | NA | null | null | 1 | 0 | Normal | 102.8571 | 4.8637 | 8
57 | Chemical Tank - NaOH | DS1 Slight | no | Lognormal | 0.13 | 0 | 0.5 | NA | null | null | 0.1 | 0.95 | Normal | 5 | 0.60796 | 1 | Assigned fragility of algorithm for: `Chemical Tanks`
58 | Chemical Tank - NaOH | DS2 Moderate | no | Lognormal | 0.3 | 0 | 0.5 | NA | null | null | 0.4 | 0.75 | Normal | 20 | 1.2159 | 2
59 | Chemical Tank - NaOH | DS3 Extensive | no | Lognormal | 0.5 | 0 | 0.6 | NA | null | null | 0.8 | 0.3 | Normal | 50 | 2.4318 | 4
60 | Chemical Tank - NaOH | DS4 Complete | no | Lognormal | 1.05 | 0 | 0.6 | NA | null | null | 1 | 0 | Normal | 102.8571 | 4.8637 | 8
61 | Chlorination Equipment | DS1 Slight | no | Lognormal | 0.23 | 0 | 0.25 | NA | null | null | 0.15 | 0.95 | Normal | 1 | 0.30398 | 0.5 | Assigned fragility of algorithm for: `Building 0.15g`
62 | Chlorination Equipment | DS2 Moderate | no | Lognormal | 0.38 | 0 | 0.35 | NA | null | null | 0.5 | 0.75 | Normal | 3 | 0.60796 | 1
63 | Chlorination Equipment | DS3 Extensive | no | Lognormal | 0.55 | 0 | 0.4 | NA | null | null | 0.8 | 0.3 | Normal | 15 | 1.8239 | 3
64 | Chlorination Equipment | DS4 Complete | no | Lognormal | 0.8 | 0 | 0.4 | NA | null | null | 0.97 | 0 | Normal | 30 | 2.4318 | 4
65 | Compressed Air Vessel | DS1 Slight | no | Lognormal | 0.2 | 0 | 0.5 | NA | null | null | 0.1 | 0.95 | Normal | 5 | 0.60796 | 1 | Assigned fragility of algorithm for: 'Air Tank Vertical`
66 | Compressed Air Vessel | DS2 Moderate | no | Lognormal | 0.25 | 0 | 0.5 | NA | null | null | 0.4 | 0.75 | Normal | 20 | 1.2159 | 2 | Assigned fragility of algorithm for: 'Air Tank Vertical`
67 | Compressed Air Vessel | DS3 Extensive | no | Lognormal | 0.3 | 0 | 0.5 | NA | null | null | 0.8 | 0.3 | Normal | 50 | 2.4318 | 4 | Assigned fragility of algorithm for: 'Air Tank Vertical`
68 | Compressed Air Vessel | DS4 Complete | no | Lognormal | 0.5 | 0 | 0.5 | NA | null | null | 1 | 0 | Normal | 102.8571 | 4.8637 | 8 | Assigned fragility of algorithm for: 'Air Tank Vertical`
69 | RC Tank On Ground - Anchored | DS1 Slight | no | Lognormal | 0.25 | 0 | 0.55 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | HAZUS algorithm for Concrete Tank On-ground, Anchored. NIBS 2004, Table 8.9.
70 | RC Tank On Ground - Anchored | DS2 Moderate | no | Lognormal | 0.52 | 0 | 0.7 | NA | null | null | 0.7 | 0.75 | Normal | 20 | 1.2159 | 2 | HAZUS algorithm for Concrete Tank On-ground, Anchored. NIBS 2004, Table 8.9.
71 | RC Tank On Ground - Anchored | DS3 Extensive | no | Lognormal | 0.95 | 0 | 0.6 | NA | null | null | 0.85 | 0.3 | Normal | 60 | 2.4318 | 4 | HAZUS algorithm for Concrete Tank On-ground, Anchored. NIBS 2004, Table 8.9.
72 | RC Tank On Ground - Anchored | DS4 Complete | no | Lognormal | 1.64 | 0 | 0.7 | NA | null | null | 0.99 | 0 | Normal | 102.8571 | 4.8637 | 8 | HAZUS algorithm for Concrete Tank On-ground, Anchored. NIBS 2004, Table 8.9.
73 | Concrete Tank 10X20 BACRINSE | DS1 Slight | no | Lognormal | 0.25 | 0 | 0.55 | NA | null | null | 0.2 | 0.95 | Normal | 2 | 0.60796 | 1 | Assigned fragility of algorithm for: `RC Tank On Ground - Anchored`
74 | Concrete Tank 10X20 BACRINSE | DS2 Moderate | no | Lognormal | 0.52 | 0 | 0.7 | NA | null | null | 0.7 | 0.75 | Normal | 5 | 1.2159 | 2
75 | Concrete Tank 10X20 BACRINSE | DS3 Extensive | no | Lognormal | 0.95 | 0 | 0.6 | NA | null | null | 0.85 | 0.3 | Normal | 10 | 2.4318 | 4
76 | Concrete Tank 10X20 BACRINSE | DS4 Complete | no | Lognormal | 1.64 | 0 | 0.7 | NA | null | null | 0.99 | 0 | Normal | 21 | 4.8637 | 8
77 | Concrete Tank 20x20 BKWSH | DS1 Slight | no | Lognormal | 0.25 | 0 | 0.55 | NA | null | null | 0.2 | 0.95 | Normal | 2 | 0.60796 | 1 | Assigned fragility of algorithm for: `RC Tank On Ground - Anchored`
78 | Concrete Tank 20x20 BKWSH | DS2 Moderate | no | Lognormal | 0.52 | 0 | 0.7 | NA | null | null | 0.7 | 0.75 | Normal | 5 | 1.2159 | 2
79 | Concrete Tank 20x20 BKWSH | DS3 Extensive | no | Lognormal | 0.95 | 0 | 0.6 | NA | null | null | 0.85 | 0.3 | Normal | 10 | 2.4318 | 4
80 | Concrete Tank 20x20 BKWSH | DS4 Complete | no | Lognormal | 1.64 | 0 | 0.7 | NA | null | null | 0.99 | 0 | Normal | 21 | 4.8637 | 8
81 | Concrete Tank 20x20 CLCONTACT | DS1 Slight | no | Lognormal | 0.25 | 0 | 0.55 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | Assigned fragility of algorithm for: `RC Tank On Ground - Anchored`
82 | Concrete Tank 20x20 CLCONTACT | DS2 Moderate | no | Lognormal | 0.52 | 0 | 0.7 | NA | null | null | 0.7 | 0.75 | Normal | 20 | 1.2159 | 2
83 | Concrete Tank 20x20 CLCONTACT | DS3 Extensive | no | Lognormal | 0.95 | 0 | 0.6 | NA | null | null | 0.85 | 0.3 | Normal | 60 | 2.4318 | 4
84 | Concrete Tank 20x20 CLCONTACT | DS4 Complete | no | Lognormal | 1.64 | 0 | 0.7 | NA | null | null | 0.99 | 0 | Normal | 102.8571 | 4.8637 | 8
85 | Concrete Tank 20x25 FLOC | DS1 Slight | no | Lognormal | 0.25 | 0 | 0.55 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | Assigned fragility of algorithm for: `RC Tank On Ground - Anchored`
86 | Concrete Tank 20x25 FLOC | DS2 Moderate | no | Lognormal | 0.52 | 0 | 0.7 | NA | null | null | 0.7 | 0.75 | Normal | 20 | 1.2159 | 2
87 | Concrete Tank 20x25 FLOC | DS3 Extensive | no | Lognormal | 0.95 | 0 | 0.6 | NA | null | null | 0.85 | 0.3 | Normal | 60 | 2.4318 | 4
88 | Concrete Tank 20x25 FLOC | DS4 Complete | no | Lognormal | 1.64 | 0 | 0.7 | NA | null | null | 0.99 | 0 | Normal | 102.8571 | 4.8637 | 8
89 | Concrete Tank 20x25 WASHWATER | DS1 Slight | no | Lognormal | 0.25 | 0 | 0.55 | NA | null | null | 0.2 | 0.95 | Normal | 1 | 0.60796 | 1 | Assigned fragility of algorithm for: `RC Tank On Ground - Anchored`
90 | Concrete Tank 20x25 WASHWATER | DS2 Moderate | no | Lognormal | 0.52 | 0 | 0.7 | NA | null | null | 0.7 | 0.75 | Normal | 7 | 1.2159 | 2
91 | Concrete Tank 20x25 WASHWATER | DS3 Extensive | no | Lognormal | 0.95 | 0 | 0.6 | NA | null | null | 0.85 | 0.3 | Normal | 20 | 2.4318 | 4
92 | Concrete Tank 20x25 WASHWATER | DS4 Complete | no | Lognormal | 1.64 | 0 | 0.7 | NA | null | null | 0.99 | 0 | Normal | 40 | 4.8637 | 8
93 | Concrete Tank 20x80 BACFILTER | DS1 Slight | no | Lognormal | 0.25 | 0 | 0.55 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | Assigned fragility of algorithm for: `RC Tank On Ground - Anchored`
94 | Concrete Tank 20x80 BACFILTER | DS2 Moderate | no | Lognormal | 0.52 | 0 | 0.7 | NA | null | null | 0.7 | 0.75 | Normal | 20 | 1.2159 | 2
95 | Concrete Tank 20x80 BACFILTER | DS3 Extensive | no | Lognormal | 0.95 | 0 | 0.6 | NA | null | null | 0.85 | 0.3 | Normal | 60 | 2.4318 | 4
96 | Concrete Tank 20x80 BACFILTER | DS4 Complete | no | Lognormal | 1.64 | 0 | 0.7 | NA | null | null | 0.99 | 0 | Normal | 102.8571 | 4.8637 | 8
97 | Concrete Tank 30x30 CLRWTR | DS1 Slight | no | Lognormal | 0.25 | 0 | 0.55 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | Assigned fragility of algorithm for: `RC Tank On Ground - Anchored`
98 | Concrete Tank 30x30 CLRWTR | DS2 Moderate | no | Lognormal | 0.52 | 0 | 0.7 | NA | null | null | 0.7 | 0.75 | Normal | 20 | 1.2159 | 2
99 | Concrete Tank 30x30 CLRWTR | DS3 Extensive | no | Lognormal | 0.95 | 0 | 0.6 | NA | null | null | 0.85 | 0.3 | Normal | 60 | 2.4318 | 4
100 | Concrete Tank 30x30 CLRWTR | DS4 Complete | no | Lognormal | 1.64 | 0 | 0.7 | NA | null | null | 0.99 | 0 | Normal | 102.8571 | 4.8637 | 8
101 | Concrete Tank 30x70 DAFF | DS1 Slight | no | Lognormal | 0.25 | 0 | 0.55 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | Assigned fragility of algorithm for: `RC Tank On Ground - Anchored`
102 | Concrete Tank 30x70 DAFF | DS2 Moderate | no | Lognormal | 0.52 | 0 | 0.7 | NA | null | null | 0.7 | 0.75 | Normal | 20 | 1.2159 | 2
103 | Concrete Tank 30x70 DAFF | DS3 Extensive | no | Lognormal | 0.95 | 0 | 0.6 | NA | null | null | 0.85 | 0.3 | Normal | 60 | 2.4318 | 4
104 | Concrete Tank 30x70 DAFF | DS4 Complete | no | Lognormal | 1.64 | 0 | 0.7 | NA | null | null | 0.99 | 0 | Normal | 102.8571 | 4.8637 | 8
105 | Concrete Tank BALANCING | DS1 Slight | no | Lognormal | 0.25 | 0 | 0.55 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | Assigned fragility of algorithm for: `RC Tank On Ground - Anchored`
106 | Concrete Tank BALANCING | DS2 Moderate | no | Lognormal | 0.52 | 0 | 0.7 | NA | null | null | 0.7 | 0.75 | Normal | 20 | 1.2159 | 2
107 | Concrete Tank BALANCING | DS3 Extensive | no | Lognormal | 0.95 | 0 | 0.6 | NA | null | null | 0.85 | 0.3 | Normal | 60 | 2.4318 | 4
108 | Concrete Tank BALANCING | DS4 Complete | no | Lognormal | 1.64 | 0 | 0.7 | NA | null | null | 0.99 | 0 | Normal | 102.8571 | 4.8637 | 8
109 | Diesel Storage Tank Horizontal | DS1 Slight | no | Lognormal | 0.1 | 0 | 0.5 | NA | null | null | 0.2 | 0.95 | Normal | 1 | 0.60796 | 1 | GA adaptation of HAZUS algorithm for `Chlorination Equipment`. NIBS 2003, Table A.8.6, Table 15B.5. | Shifted slightly to right and steepened due to absence of base fixity. Extensive damage much less likely as tank will not overturn and slide as rigid body.
110 | Diesel Storage Tank Horizontal | DS2 Moderate | no | Lognormal | 0.2 | 0 | 0.5 | NA | null | null | 0.7 | 0.75 | Normal | 2 | 1.2159 | 2
111 | Diesel Storage Tank Horizontal | DS3 Extensive | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.85 | 0.3 | Normal | 5 | 2.4318 | 4
112 | Diesel Storage Tank Horizontal | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.99 | 0 | Normal | 10 | 4.8637 | 8
113 | Electrical Kiosk Switchroom | DS1 Slight | no | Lognormal | 0.4 | 0 | 0.6 | NA | null | null | 0.2 | 0.95 | Normal | 1 | 0.60796 | 1
114 | Electrical Kiosk Switchroom | DS2 Moderate | no | Lognormal | 0.67 | 0 | 0.7 | NA | null | null | 0.7 | 0.75 | Normal | 3 | 1.2159 | 2
115 | Electrical Kiosk Switchroom | DS3 Extensive | no | Lognormal | 0.85 | 0 | 0.7 | NA | null | null | 0.85 | 0.3 | Normal | 5 | 2.4318 | 4
116 | Electrical Kiosk Switchroom | DS4 Complete | no | Lognormal | 1 | 0 | 0.7 | NA | null | null | 0.99 | 0 | Normal | 10 | 4.8637 | 8
117 | Transformer | DS1 Slight | no | Lognormal | 0.1 | 0 | 0.5 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | EPN14 115/12KV | Slight and moderate as per diesel tank. EPN14 for sliding failure but moved 0.1g to right (very similar to diesel tank). EPN14 for overturning.
118 | Transformer | DS2 Moderate | no | Lognormal | 0.21 | 0 | 0.5 | NA | null | null | 0.7 | 0.75 | Normal | 20 | 1.2159 | 2
119 | Transformer | DS3 Extensive | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.85 | 0.3 | Normal | 60 | 2.4318 | 4
120 | Transformer | DS4 Complete | no | Lognormal | 0.8 | 0 | 0.39 | NA | null | null | 0.99 | 0 | Normal | 102.8571 | 4.8637 | 8
121 | Transformer Dry Type | DS1 Slight | no | Lognormal | 0.1 | 0 | 0.5 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | Adapted from EPN14 115/12KV
122 | Transformer Dry Type | DS2 Moderate | no | Lognormal | 0.21 | 0 | 0.5 | NA | null | null | 0.7 | 0.75 | Normal | 20 | 1.2159 | 2
123 | Transformer Dry Type | DS3 Extensive | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.85 | 0.3 | Normal | 60 | 2.4318 | 4
124 | Transformer Dry Type | DS4 Complete | no | Lognormal | 0.4 | 0 | 0.39 | NA | null | null | 0.99 | 0 | Normal | 102.8571 | 4.8637 | 8
125 | Electrical Kiosk Transformer 433V | DS1 Slight | no | Lognormal | 0.1 | 0 | 0.5 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | Assigned fragility of algorithm for: `Transformer`.
126 | Electrical Kiosk Transformer 433V | DS2 Moderate | no | Lognormal | 0.21 | 0 | 0.5 | NA | null | null | 0.7 | 0.75 | Normal | 20 | 1.2159 | 2
127 | Electrical Kiosk Transformer 433V | DS3 Extensive | no | Lognormal | 0.8 | 0 | 0.39 | NA | null | null | 0.85 | 0.3 | Normal | 60 | 2.4318 | 4
128 | Electrical Kiosk Transformer 433V | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.99 | 0 | Normal | 102.8571 | 4.8637 | 8
129 | Electrical Transformer 22kV Oil-Filled | DS1 Slight | no | Lognormal | 0.1 | 0 | 0.5 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | Assigned fragility of algorithm for: `Transformer`.
130 | Electrical Transformer 22kV Oil-Filled | DS2 Moderate | no | Lognormal | 0.21 | 0 | 0.5 | NA | null | null | 0.7 | 0.75 | Normal | 20 | 1.2159 | 2
131 | Electrical Transformer 22kV Oil-Filled | DS3 Extensive | no | Lognormal | 0.8 | 0 | 0.39 | NA | null | null | 0.85 | 0.3 | Normal | 60 | 2.4318 | 4
132 | Electrical Transformer 22kV Oil-Filled | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.99 | 0 | Normal | 102.8571 | 4.8637 | 8
133 | Genset 3100kVA | DS1 Slight | no | Lognormal | 0.2 | 0 | 0.5 | NA | null | null | 0.2 | 0.95 | Normal | 1.5 | 0.60796 | 1 | GA adaptation of HAZUS algorithm for `Chlorination Equipment`. NIBS 2003, Table A.8.6, Table 15B.5.
134 | Genset 3100kVA | DS2 Moderate | no | Lognormal | 0.35 | 0 | 0.5 | NA | null | null | 0.7 | 0.75 | Normal | 3 | 1.2159 | 2
135 | Genset 3100kVA | DS3 Extensive | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.85 | 0.3 | Normal | 5 | 2.4318 | 4
136 | Genset 3100kVA | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.99 | 0 | Normal | 7 | 4.8637 | 8
137 | Steel Tank Liquid CO2 | DS1 Slight | no | Lognormal | 0.15 | 0 | 0.5 | NA | null | null | 0.2 | 0.95 | Normal | 2 | 0.60796 | 1 | <Source not appended>
138 | Steel Tank Liquid CO2 | DS2 Moderate | no | Lognormal | 0.2 | 0 | 0.5 | NA | null | null | 0.7 | 0.75 | Normal | 5 | 1.2159 | 2
139 | Steel Tank Liquid CO2 | DS3 Extensive | no | Lognormal | 0.28 | 0 | 0.52 | NA | null | null | 0.85 | 0.3 | Normal | 7 | 2.4318 | 4
140 | Steel Tank Liquid CO2 | DS4 Complete | no | Lognormal | 0.45 | 0 | 0.6 | NA | null | null | 0.99 | 0 | Normal | 14 | 4.8637 | 8
141 | Surge Vessels | DS1 Slight | no | Lognormal | 0.4 | 0 | 0.35 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | Expert Judgment
142 | Surge Vessels | DS2 Moderate | no | Lognormal | 0.45 | 0 | 0.35 | NA | null | null | 0.7 | 0.75 | Normal | 7 | 1.2159 | 2
143 | Surge Vessels | DS3 Extensive | no | Lognormal | 0.53 | 0 | 0.38 | NA | null | null | 0.85 | 0.3 | Normal | 14 | 2.4318 | 4
144 | Surge Vessels | DS4 Complete | no | Lognormal | 0.7 | 0 | 0.45 | NA | null | null | 0.99 | 0 | Normal | 28 | 4.8637 | 8
145 | Elevated Pipework | DS1 Slight | no | Lognormal | 101 | NA | 1.11 | NA | null | null | 0.2 | 0.95 | Normal | 1 | 0.12159 | 0.2 | HAZUS algorithms for `Eleveted Pipes - Anchored`. NIBS 2003, Table A.8.6, Table 15B.5.
146 | Elevated Pipework | DS2 Moderate | no | Lognormal | 101 | NA | 1.11 | NA | null | null | 0.5 | 0.75 | Normal | 2 | 0.30398 | 0.5 | HAZUS algorithms for `Eleveted Pipes - Anchored`. NIBS 2003, Table A.8.6, Table 15B.5.
147 | Elevated Pipework | DS3 Extensive | no | Lognormal | 0.53 | 0 | 0.6 | NA | null | null | 0.65 | 0.3 | Normal | 3 | 0.91194 | 1.5 | HAZUS algorithms for `Eleveted Pipes - Anchored`. NIBS 2003, Table A.8.6, Table 15B.5.
148 | Elevated Pipework | DS4 Complete | no | Lognormal | 1 | 0 | 0.6 | NA | null | null | 0.9 | 0 | Normal | 7 | 1.8239 | 3 | HAZUS algorithms for `Eleveted Pipes - Anchored`. NIBS 2003, Table A.8.6, Table 15B.5.
149 | Pipe Connector Buried | DS1 Slight | no | Lognormal | 101 | NA | 1.11 | NA | null | null | 0.2 | 0.95 | Normal | 1 | 0.60796 | 1 | Assigned fragility of algorithm for: `Elevated Pipework`
150 | Pipe Connector Buried | DS2 Moderate | no | Lognormal | 101 | NA | 1.11 | NA | null | null | 0.7 | 0.75 | Normal | 2 | 1.2159 | 2
151 | Pipe Connector Buried | DS3 Extensive | no | Lognormal | 0.53 | 0 | 0.6 | NA | null | null | 0.85 | 0.3 | Normal | 4 | 2 | 4
152 | Pipe Connector Buried | DS4 Complete | no | Lognormal | 1 | 0 | 0.6 | NA | null | null | 0.99 | 0 | Normal | 7 | 3 | 8
153 | Pipe Connector Overground | DS1 Slight | no | Lognormal | 0.4 | 0 | 0.6 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1
154 | Pipe Connector Overground | DS2 Moderate | no | Lognormal | 0.67 | 0 | 0.7 | NA | null | null | 0.7 | 0.75 | Normal | 20 | 1.2159 | 2
155 | Pipe Connector Overground | DS3 Extensive | no | Lognormal | 0.85 | 0 | 0.7 | NA | null | null | 0.85 | 0.3 | Normal | 60 | 2.4318 | 4
156 | Pipe Connector Overground | DS4 Complete | no | Lognormal | 1 | 0 | 0.7 | NA | null | null | 0.99 | 0 | Normal | 102.8571 | 4.8637 | 8
157 | Pipe Joint | DS1 Slight | no | Lognormal | 0.18 | 0 | 0.5 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | Expert Judgment
158 | Pipe Joint | DS2 Moderate | no | Lognormal | 0.3 | 0 | 0.5 | NA | null | null | 0.7 | 0.75 | Normal | 5 | 1.2159 | 2
159 | Pipe Joint | DS3 Extensive | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.85 | 0.3 | Normal | 10 | 2.4318 | 4
160 | Pipe Joint | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.99 | 0 | Normal | 21 | 4.8637 | 8
161 | Pipe Main Inlet | DS1 Slight | no | Lognormal | 101 | NA | 1.11 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | Assigned fragility of algorithm for: `Elevated Pipework`
162 | Pipe Main Inlet | DS2 Moderate | no | Lognormal | 101 | NA | 1.11 | NA | null | null | 0.7 | 0.75 | Normal | 5 | 1.2159 | 2
163 | Pipe Main Inlet | DS3 Extensive | no | Lognormal | 0.53 | 0 | 0.6 | NA | null | null | 0.85 | 0.3 | Normal | 10 | 2.4318 | 4
164 | Pipe Main Inlet | DS4 Complete | no | Lognormal | 1 | 0 | 0.6 | NA | null | null | 0.99 | 0 | Normal | 21 | 4.8637 | 8
165 | Pipe Section DN1200 | DS1 Slight | no | Lognormal | 0.18 | 0 | 0.5 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | Assigned fragility of algorithm for: `Pipe Joint`
166 | Pipe Section DN1200 | DS2 Moderate | no | Lognormal | 0.3 | 0 | 0.5 | NA | null | null | 0.7 | 0.75 | Normal | 5 | 1.2159 | 2
167 | Pipe Section DN1200 | DS3 Extensive | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.85 | 0.3 | Normal | 10 | 2.4318 | 4
168 | Pipe Section DN1200 | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.99 | 0 | Normal | 21 | 4.8637 | 8
169 | Pipe Section DN1400 | DS1 Slight | no | Lognormal | 0.18 | 0 | 0.5 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | Assigned fragility of algorithm for: `Pipe Joint`
170 | Pipe Section DN1400 | DS2 Moderate | no | Lognormal | 0.3 | 0 | 0.5 | NA | null | null | 0.7 | 0.75 | Normal | 5 | 1.2159 | 2
171 | Pipe Section DN1400 | DS3 Extensive | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.85 | 0.3 | Normal | 10 | 2.4318 | 4
172 | Pipe Section DN1400 | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.99 | 0 | Normal | 21 | 4.8637 | 8
173 | Pipe Section DN1700 | DS1 Slight | no | Lognormal | 0.18 | 0 | 0.5 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | Assigned fragility of algorithm for: `Pipe Joint`
174 | Pipe Section DN1700 | DS2 Moderate | no | Lognormal | 0.3 | 0 | 0.5 | NA | null | null | 0.7 | 0.75 | Normal | 5 | 1.2159 | 2
175 | Pipe Section DN1700 | DS3 Extensive | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.85 | 0.3 | Normal | 10 | 2.4318 | 4
176 | Pipe Section DN1700 | DS4 Complete | no | Lognormal | 101 | 0 | 1.11 | NA | null | null | 0.99 | 0 | Normal | 21 | 4.8637 | 8
177 | Pump Horizontal 1600kW | DS1 Slight | no | Lognormal | 0.13 | 0 | 0.6 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | HAZUS algorithm for `Pumping Station - Small with Unanchored Components`. NIBS 2004, Table 8.6.
178 | Pump Horizontal 1600kW | DS2 Moderate | no | Lognormal | 0.28 | 0 | 0.5 | NA | null | null | 0.7 | 0.75 | Normal | 20 | 1.2159 | 2
179 | Pump Horizontal 1600kW | DS3 Extensive | no | Lognormal | 0.66 | 0 | 0.65 | NA | null | null | 0.85 | 0.3 | Normal | 60 | 2.4318 | 4
180 | Pump Horizontal 1600kW | DS4 Complete | no | Lognormal | 1.5 | 0 | 0.8 | NA | null | null | 0.99 | 0 | Normal | 102.8571 | 4.8637 | 8
181 | Pump Backwash | DS1 Slight | no | Lognormal | 0.23 | 0 | 0.7 | NA | null | null | 0.2 | 0.95 | Normal | 3 | 0.60796 | 1 | GA adaptation of HAZUS algorithm for `Pumping Station - Small with Anchored Components`. NIBS 2004, Table 8.6. | Shifted right 0.08g due to greater resilience.
182 | Pump Backwash | DS2 Moderate | no | Lognormal | 0.44 | 0 | 0.65 | NA | null | null | 0.7 | 0.75 | Normal | 20 | 1.2159 | 2
183 | Pump Backwash | DS3 Extensive | no | Lognormal | 0.74 | 0 | 0.65 | NA | null | null | 0.85 | 0.3 | Normal | 60 | 2.4318 | 4
184 | Pump Backwash | DS4 Complete | no | Lognormal | 1.58 | 0 | 0.8 | NA | null | null | 0.99 | 0 | Normal | 102.8571 | 4.8637 | 8
185 | UV Dosing Equipment | DS1 Slight | no | Lognormal | 101 | NA | 1.11 | NA | null | null | 0 | 0.95 | Normal | 0 | 0.60796 | 1 | Assigned fragility of algorithm for: `Elevated Pipework`
186 | UV Dosing Equipment | DS2 Moderate | no | Lognormal | 101 | NA | 1.11 | NA | null | null | 0 | 0.75 | Normal | 0 | 1.2159 | 2
187 | UV Dosing Equipment | DS3 Extensive | no | Lognormal | 0.53 | 0 | 0.6 | NA | null | null | 0.85 | 0.3 | Normal | 60 | 2.4318 | 4
188 | UV Dosing Equipment | DS4 Complete | no | Lognormal | 1 | 0 | 0.6 | NA | null | null | 0.99 | 0 | Normal | 102.8571 | 4.8637 | 8

## damage_state_def
component_type | damage_state | damage_state_definition
Electric Power Commercial | DS1 Slight | Power source to model. Assumed seismically invulnerable for simulation purposes.
Electric Power Commercial | DS2 Moderate | Power source to model. Assumed seismically invulnerable for simulation purposes.
Electric Power Commercial | DS3 Extensive | Power source to model. Assumed seismically invulnerable for simulation purposes.
Electric Power Commercial | DS4 Complete | Power source to model. Assumed seismically invulnerable for simulation purposes.
SYSTEM_INPUT | DS1 Slight | Model artefact. Assumed seismically invulnerable for simulation purposes.
SYSTEM_INPUT | DS2 Moderate | Model artefact. Assumed seismically invulnerable for simulation purposes.
SYSTEM_INPUT | DS3 Extensive | Model artefact. Assumed seismically invulnerable for simulation purposes.
SYSTEM_INPUT | DS4 Complete | Model artefact. Assumed seismically invulnerable for simulation purposes.
SYSTEM_OUTPUT | DS1 Slight | Model artefact. Assumed seismically invulnerable for simulation purposes.
SYSTEM_OUTPUT | DS2 Moderate | Model artefact. Assumed seismically invulnerable for simulation purposes.
SYSTEM_OUTPUT | DS3 Extensive | Model artefact. Assumed seismically invulnerable for simulation purposes.
SYSTEM_OUTPUT | DS4 Complete | Model artefact. Assumed seismically invulnerable for simulation purposes.
JUNCTION | DS1 Slight | Model artefact. Assumed seismically invulnerable for simulation purposes.
JUNCTION | DS2 Moderate | Model artefact. Assumed seismically invulnerable for simulation purposes.
JUNCTION | DS3 Extensive | Model artefact. Assumed seismically invulnerable for simulation purposes.
JUNCTION | DS4 Complete | Model artefact. Assumed seismically invulnerable for simulation purposes.
Air Tank Vertical | DS1 Slight | Minor base movement with yield of HD bolts
Air Tank Vertical | DS2 Moderate | Major elongation of HD bolts
Air Tank Vertical | DS3 Extensive | Overturning but checked by building structure (25% as likely as full overturning)
Air Tank Vertical | DS4 Complete | Overturning
Building 0.15g | DS1 Slight | <add definition>
Building 0.15g | DS2 Moderate | <add definition>
Building 0.15g | DS3 Extensive | <add definition>
Building 0.15g | DS4 Complete | <add definition>
Chemical Building | DS1 Slight | <add definition>
Chemical Building | DS2 Moderate | <add definition>
Chemical Building | DS3 Extensive | <add definition>
Chemical Building | DS4 Complete | <add definition>
Chemical Dosing Panel | DS1 Slight | Partial overturning without equipment damage in panel
Chemical Dosing Panel | DS2 Moderate | Overturning with damage to dosing equipment components
Chemical Dosing Panel | DS3 Extensive | NA
Chemical Dosing Panel | DS4 Complete | NA
Chemical Tanks | DS1 Slight | Damage to HDPE at HD bolt.
Chemical Tanks | DS2 Moderate | Extensive tearing and tank movement.
Chemical Tanks | DS3 Extensive | Major tank movement on pedestal.
Chemical Tanks | DS4 Complete | Ruptured tank.
Chemical Tank - ALUM | DS1 Slight
Chemical Tank - ALUM | DS2 Moderate
Chemical Tank - ALUM | DS3 Extensive
Chemical Tank - ALUM | DS4 Complete
Chemical Tank - FSA | DS1 Slight
Chemical Tank - FSA | DS2 Moderate
Chemical Tank - FSA | DS3 Extensive
Chemical Tank - FSA | DS4 Complete
Chemical Tank - NaOH | DS1 Slight
Chemical Tank - NaOH | DS2 Moderate
Chemical Tank - NaOH | DS3 Extensive
Chemical Tank - NaOH | DS4 Complete
Chlorination Equipment | DS1 Slight
Chlorination Equipment | DS2 Moderate
Chlorination Equipment | DS3 Extensive
Chlorination Equipment | DS4 Complete
Compressed Air Vessel | DS1 Slight
Compressed Air Vessel | DS2 Moderate
Compressed Air Vessel | DS3 Extensive
Compressed Air Vessel | DS4 Complete
RC Tank On Ground - Anchored | DS1 Slight
RC Tank On Ground - Anchored | DS2 Moderate
RC Tank On Ground - Anchored | DS3 Extensive
RC Tank On Ground - Anchored | DS4 Complete
Concrete Tank 10X20 BACRINSE | DS1 Slight
Concrete Tank 10X20 BACRINSE | DS2 Moderate
Concrete Tank 10X20 BACRINSE | DS3 Extensive
Concrete Tank 10X20 BACRINSE | DS4 Complete
Concrete Tank 20x20 BKWSH | DS1 Slight
Concrete Tank 20x20 BKWSH | DS2 Moderate
Concrete Tank 20x20 BKWSH | DS3 Extensive
Concrete Tank 20x20 BKWSH | DS4 Complete
Concrete Tank 20x20 CLCONTACT | DS1 Slight
Concrete Tank 20x20 CLCONTACT | DS2 Moderate
Concrete Tank 20x20 CLCONTACT | DS3 Extensive
Concrete Tank 20x20 CLCONTACT | DS4 Complete
Concrete Tank 20x25 FLOC | DS1 Slight
Concrete Tank 20x25 FLOC | DS2 Moderate
Concrete Tank 20x25 FLOC | DS3 Extensive
Concrete Tank 20x25 FLOC | DS4 Complete
Concrete Tank 20x25 WASHWATER | DS1 Slight
Concrete Tank 20x25 WASHWATER | DS2 Moderate
Concrete Tank 20x25 WASHWATER | DS3 Extensive
Concrete Tank 20x25 WASHWATER | DS4 Complete
Concrete Tank 20x80 BACFILTER | DS1 Slight
Concrete Tank 20x80 BACFILTER | DS2 Moderate
Concrete Tank 20x80 BACFILTER | DS3 Extensive
Concrete Tank 20x80 BACFILTER | DS4 Complete
Concrete Tank 30x30 CLRWTR | DS1 Slight
Concrete Tank 30x30 CLRWTR | DS2 Moderate
Concrete Tank 30x30 CLRWTR | DS3 Extensive
Concrete Tank 30x30 CLRWTR | DS4 Complete
Concrete Tank 30x70 DAFF | DS1 Slight
Concrete Tank 30x70 DAFF | DS2 Moderate
Concrete Tank 30x70 DAFF | DS3 Extensive
Concrete Tank 30x70 DAFF | DS4 Complete
Concrete Tank BALANCING | DS1 Slight
Concrete Tank BALANCING | DS2 Moderate
Concrete Tank BALANCING | DS3 Extensive
Concrete Tank BALANCING | DS4 Complete
Diesel Storage Tank Horizontal | DS1 Slight | Minor base movement.
Diesel Storage Tank Horizontal | DS2 Moderate | Extensive movement without overturning with damage to pipework.
Diesel Storage Tank Horizontal | DS3 Extensive | NA
Diesel Storage Tank Horizontal | DS4 Complete | NA
Elevated Pipework | DS1 Slight | Damage to HDPE at HD bolt.
Elevated Pipework | DS2 Moderate | Extensive tearing and tank movement.
Elevated Pipework | DS3 Extensive | Major tanle movement on pedestal.
Elevated Pipework | DS4 Complete | Ruptured tank.
Electrical Kiosk Switchroom | DS1 Slight
Electrical Kiosk Switchroom | DS2 Moderate
Electrical Kiosk Switchroom | DS3 Extensive
Electrical Kiosk Switchroom | DS4 Complete
Electrical Kiosk Transformer 433V | DS1 Slight
Electrical Kiosk Transformer 433V | DS2 Moderate
Electrical Kiosk Transformer 433V | DS3 Extensive
Electrical Kiosk Transformer 433V | DS4 Complete
Electrical Transformer 22kV Oil-Filled | DS1 Slight
Electrical Transformer 22kV Oil-Filled | DS2 Moderate
Electrical Transformer 22kV Oil-Filled | DS3 Extensive
Electrical Transformer 22kV Oil-Filled | DS4 Complete
Genset 3100kVA | DS1 Slight | Minor base movement.
Genset 3100kVA | DS2 Moderate | Extensive movement without overturning with damage to fuel supply pipework and cabling.
Genset 3100kVA | DS3 Extensive | Not likely.
Genset 3100kVA | DS4 Complete | Not likely.
Switchrooms | DS1 Slight | <add definition>
Switchrooms | DS2 Moderate | <add definition>
Switchrooms | DS3 Extensive | <add definition>
Switchrooms | DS4 Complete | <add definition>
Transformer | DS1 Slight | Minor base movement.
Transformer | DS2 Moderate | Extensive sliding damage to cables of transformer.
Transformer | DS3 Extensive | NA
Transformer | DS4 Complete | Overturning.
Transformer Dry Type | DS1 Slight | Minor base movement.
Transformer Dry Type | DS2 Moderate | Extensive sliding damage to cables of transformer.
Transformer Dry Type | DS3 Extensive | NA
Transformer Dry Type | DS4 Complete | Internal overturning of air cooled core.
Steel Tank Liquid CO2 | DS1 Slight | Minor base movement with yield of HD bolts.
Steel Tank Liquid CO2 | DS2 Moderate | Moderate major elongation of HD bolts.
Steel Tank Liquid CO2 | DS3 Extensive | Extensive overturning but checked by Chem buildings (25% as likely as full overturning).
Steel Tank Liquid CO2 | DS4 Complete | Complete overturning .
Surge Vessels | DS1 Slight | Minor base movement with yield of HD bolts
Surge Vessels | DS2 Moderate | Moderate majorelongation of HD bolts
Surge Vessels | DS3 Extensive | Extensive overturning but checked by Chem buildings (25% as likely as full overturning)
Surge Vessels | DS4 Complete | Complete overturning
Pipe Connector Buried | DS1 Slight
Pipe Connector Buried | DS2 Moderate
Pipe Connector Buried | DS3 Extensive
Pipe Connector Buried | DS4 Complete
Pipe Connector Overground | DS1 Slight
Pipe Connector Overground | DS2 Moderate
Pipe Connector Overground | DS3 Extensive
Pipe Connector Overground | DS4 Complete
Pipe Joint | DS1 Slight | Leakage
Pipe Joint | DS2 Moderate | Break
Pipe Joint | DS3 Extensive | NA
Pipe Joint | DS4 Complete | NA
Pipe Main Inlet | DS1 Slight
Pipe Main Inlet | DS2 Moderate
Pipe Main Inlet | DS3 Extensive
Pipe Main Inlet | DS4 Complete
Pipe Section DN1200 | DS1 Slight
Pipe Section DN1200 | DS2 Moderate
Pipe Section DN1200 | DS3 Extensive
Pipe Section DN1200 | DS4 Complete
Pipe Section DN1400 | DS1 Slight
Pipe Section DN1400 | DS2 Moderate
Pipe Section DN1400 | DS3 Extensive
Pipe Section DN1400 | DS4 Complete
Pump Horizontal 1600kW | DS1 Slight | Malfunction of plant for a short time (<3 days) due to electric power loss or slight building damage. [SRM-LIFE (2007)]
Pump Horizontal 1600kW | DS2 Moderate | Loss of electric power for about a week, considerable damage to mechanical and electrical equipment, or moderate building damage. [SRM-LIFE (2007)]
Pump Horizontal 1600kW | DS3 Extensive | Extensive building damage or extensive, beyond repair, pump damage. [SRM-LIFE (2007)]
Pump Horizontal 1600kW | DS4 Complete | Building collapse. [SRM-LIFE (2007)]
Pump Backwash | DS1 Slight | Malfunction of plant for a short time (<3 days) due to electric power loss or slight building damage. [SRM-LIFE (2007)]
Pump Backwash | DS2 Moderate | Loss of electric power for about a week, considerable damage to mechanical and electrical equipment, or moderate building damage. [SRM-LIFE (2007)]
Pump Backwash | DS3 Extensive | Extensive building damage or extensive, beyond repair, pump damage. [SRM-LIFE (2007)]
Pump Backwash | DS4 Complete | Building collapse. [SRM-LIFE (2007)]
UV Dosing Equipment | DS1 Slight
UV Dosing Equipment | DS2 Moderate
UV Dosing Equipment | DS3 Extensive
UV Dosing Equipment | DS4 Complete
Basins | DS1 Slight
Basins | DS2 Moderate
Basins | DS3 Extensive
Basins | DS4 Complete
Pump Horizontal - HAZUS-A | DS1 Slight
Pump Horizontal - HAZUS-A | DS2 Moderate
Pump Horizontal - HAZUS-A | DS3 Extensive
Pump Horizontal - HAZUS-A | DS4 Complete
Pump Vertical - HAZUS-A | DS1 Slight
Pump Vertical - HAZUS-A | DS2 Moderate
Pump Vertical - HAZUS-A | DS3 Extensive
Pump Vertical - HAZUS-A | DS4 Complete

## VALIDATION_TABLES
INFRASTRUCTURE_LEVEL | SYSTEM_CLASSES | RESTORATION_TIME_UNIT | COMPONENT_LOCATION_CONF
facility | PowerStation | days | defined
network | Substation | weeks | undefined
| PotableWaterTreatmentPlant | months
| PWTP | years
WasteWaterTreatmentPlant
WWTP

## asset_names
Component Types | Synonyms | Note
Baffles
Basins
Building 0.15g
Chemical Building
Chemical Dosing Panel
Chemical Tank - ALUM | Chemical Tank - Fibreglass - ALUM | D4.5m, H3.1m, Capacity 40m3
Chemical Tank - FSA |  | D2.25m, H3.5m
Chemical Tank - NaOH | Chemical Tank - Fibreglass - NaOH | D4.5m, H3.1m, Capacity 40m3
Chemical Tanks
Chlorination Equipment | Chlorination Equipment - Chlorine
Chlorine Storage Building
Circular Clarification Tank
Compressed Air Vessel
Concrete Tank 10x10 | Thickened Sludge Tank & Pumps | 10 x 10
Concrete Tank 10X20 BACRINSE | BAC Rinse & Supernatant Tank | 10 x 20
Concrete Tank 20x20 BKWSH | Backwash Water Storage Tank | 20 x 20
Concrete Tank 20x20 CLCONTACT | Chlorine Contact Tank | 20 x 20
Concrete Tank 20x25 FLOC | Flocculation Tanks | 20 x 25
Concrete Tank 20x25 WASHWATER | Washwater Tank & Recovery Pumps | 20 x 25
Concrete Tank 20x80 BACFILTER | BAC Filters | 20 x 80
Concrete Tank 30x30 CLRWTR | Clearwater Storage Tank No.1 | 30 x 30
Concrete Tank 30x70 DAFF | DAFF Tanks | 30 x 70
Concrete Tank BALANCING | Balancing Tank
Diesel Storage Tank Horizontal
Electric Power Backup
Electric Power Commercial
Electric Switchboard
Electrical HV Switchroom
Electrical HV-LV Switchroom
Electrical Kiosk Switchroom
Electrical Kiosk Transformer
Electrical Kiosk Transformer 433V
Electrical Transformer 22kV Oil-Filled
Elevated Pipework
Flow Equalisation Basin
Genset 3100kVA
Grit Chamber
JUNCTION
Paddles
Pipe Connector Buried
Pipe Connector Overground
Pipe Connector Suspended
Pipe Joint
Pipe Main Inlet
Pipe Section DN1200
Pipe Section DN1400
Pipe Section DN1700
Pipework Internal
Primary Clarifier Tank
Pump Backwash
Pump Horizontal - HAZUS-A
Pump Vertical - HAZUS-A
Pump Horizontal 1600kW
Pump Station
RC Tank On Ground - Anchored
Rectangular Sedimentation Tank
Reservoir
Scrapers
Secondary Treatment Tank
Sediment Flocculation
Sludge Digesters
Steel Tank Liquid CO2
Step Screens
Supernatant Pump Filter
SUPPLY_NODES
Surge Vessels
Switchrooms
SYSTEM_INPUT
SYSTEM_OUTPUT
Transformer
Transformer Dry Type
UV Dosing Equipment | Dosing Equipment - UV
Air Tank Vertical
Voltage Transformer
Wells

## excluded_components
C36_Post_Dosing_Static_Mixer | >> consider as part of pipe
C37A_Pre_Dosing_Static_Mixer_A | >> consider as part of pipe
C38_Service_Water_Pump_Stn | >> needed for dilution of chemicals
C44_Predosing_Analyser_Room
C45_Post_Dosing_Analyser_Room
C46_Lime_Storage_Dosing | >> not used (purpose is to reduce alkalinity in water to reduce pipe corrosion)
C51_Inlet_Flow_Meter | >> consider as part of pipe
C58_Delivery_Flow_Meter | >> consider as part of pipe
C53_Stabilisation_Flow_Meter | >> consider as part of pipe

## Tanks
Table 3 WTP - Summary of Sensitive Structures (pg 13)
Platform Number | Structure Number | Description | Approx. Plan Dimension (m) | Proposed Cut / Fill Earthworks
1 | 1 | Flocculation Tanks | 20 x 25 | Cut (4 to 7m)
2 | 2 | DAFF Tanks | 30 x 70 | Cut (0 to 4m)
3 | 7 | BAC Filters | 20 x 80 | Cut (to 4m) / Fill (to 4m)
3 | 9 | Backwash Water Storage Tank | 20 x 20 | Cut (3 to 4m)
4 | 12 | Chlorine Contact Tank | 20 x 20 | Cut (1 to 4m)
4 | 22 | Washwater Tank & Recovery Pumps | 20 x 25 | Fill (1 to 4m)
4 | 25 | Thickened Sludge Tank & Pumps | 10 x 10 | Fill (1m)
5 | 14 | Clearwater Storage Tank No.1 | 30 x 30 | Cut (0 to 2m)
5 | 15 | Clearwater Storage Tank No.2 | 30 x 30 | Cut (1 to 4m)
5 | 42 | BAC Rinse & Supernatant Tank | 10 x 20 | Cut (0 to 2m)
61/27259/113942 | Mundaring WTP and Mundaring Pumping Station C
Foundation Design Report