## table_description
table | description | note
component_list | This file lists the instances of various component types within the system. | Cost fractions define economic value of the individual component relative to the cost of entire system. Data includes a 0% allowance for components not included in the model.
component_connections | Network connections. Each pair of nodes is an edge. Directionality is defined by order of nodes in a row (Orig->Dest). | Used by: (1) network algorithm package for flow calculations, (2) Pygraphviz to draw the system layout.
supply_setup | Capacity at the output nodes on the extremity of the component network | Capacity given as percentage.
output_setup | Capacity by Generator (in MW). | Given values are the nominal generation capacities for each generator plant.
comp_type_dmg_algo | List of component types with fragility and recovery data. | Fragilities are defined according to discrete damage states. Recovery time is in WEEKS. The suffix SDL refers to component Seismic Design Level. [SDL1: 0.2g PGA, SDL2: 0.35g PGA, SDL3: 0.4g PGA].
damage_state_def | Definitions of damage states of the list of component types in the system

## component_list
component_id | component_type | component_class | cost_fraction | node_type | node_cluster | op_capacity
materiel_supply | SYSTEM_INPUT | Material Delivery and Storage | 0 | supply | INPUT | 1
node_1 | Processor A | Stage 1 processing | 0.4 | transshipment | Raw Material Supply | 1
node_2 | Processor B | Stage 2 processing | 0.2 | transshipment | Transformer | 1
node_3 | Processor C | Stage 3 processing | 0.25 | transshipment | Producer | 1
node_4 | Processor D | Stage 2 processing | 0.15 | dependency | Transformer | 1
output_1 | SYSTEM_OUTPUT | SYSTEM OUTPUT | 0 | sink | OUTPUT | 1

## component_connections
origin | destination | link_capacity | weight
materiel_supply | node_1 | 1 | 1
node_1 | node_2 | 1 | 1
node_2 | node_3 | 1 | 1
node_4 | node_2 | 1 | 1
node_3 | output_1 | 1 | 1

## supply_setup
input_node | input_capacity | capacity_fraction | commodity_type
materiel_supply | 100 | 1 | coal

## output_setup
output_node | production_node | output_node_capacity | capacity_fraction | priority
output_1 | node_y | 250 | 1 | 1

## comp_type_dmg_algo
id | component_type | damage_state | is_piecewise | damage_function | mode | median | location | beta | damage_ratio | functionality | minimum | upper_limit | lower_limit | recovery_function | recovery_mean | recovery_std | recovery_95percentile | fragility_source
1 | Processor A | DS1 Slight | yes | Lognormal | 1 | 2 | 0 | 0.375 | 0.1 | 1 | NA | 10 | null | Normal | 1 | 0.30398 | 0.5 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
2 | Processor A | DS1 Slight | yes | Lognormal | 1 | 2 | 0 | 0.375 | 0.1 | 1 | NA | 20 | 10 | Normal | 1 | 0.30398 | 0.5 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
3 | Processor A | DS1 Slight | yes | Lognormal | 1 | 2 | 0 | 0.375 | 0.1 | 1 | NA | 30 | 20 | Normal | 1 | 0.30398 | 0.5 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
4 | Processor A | DS1 Slight | yes | Lognormal | 1 | 2 | 0 | 0.375 | 0.1 | 1 | NA | null | 30 | Normal | 1 | 0.30398 | 0.5 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
5 | Processor A | DS2 Moderate | no | Lognormal | 1 | 0.57 | 0 | 0.375 | 0.3 | 0 | NA | null | null | Normal | 3 | 0.60796 | 1 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
6 | Processor A | DS3 Extensive | no | Lognormal | 1 | 0.78 | 0 | 0.475 | 0.75 | 0 | NA | null | null | Normal | 15 | 1.8239 | 3 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
7 | Processor A | DS4 Complete | no | Lognormal | 1 | 1.33 | 0 | 0.475 | 1 | 0 | NA | null | null | Normal | 30 | 2.4318 | 4 | HAZUS-MH MR3 Table 8.7 Medium/large Anchored Pumping Plants
8 | Processor B | DS1 Slight | no | Lognormal | 1 | 0.35 | 0 | 0.4 | 0.1 | 0 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | HAZUS-MH Table D8.8 Electircal equipment
9 | Processor B | DS2 Moderate | no | Lognormal | 1 | 0.55 | 0 | 0.5 | 0.3 | 0 | NA | null | null | Normal | 17 | 0.60796 | 1 | HAZUS-MH Table D8.8 Electircal equipment
10 | Processor B | DS3 Extensive | no | Lognormal | 1 | 0.75 | 0 | 0.4 | 0.75 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Sim to main feed conveyor
11 | Processor B | DS4 Complete | no | Lognormal | 1 | 1 | 0 | 0.4 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Sim to main feed conveyor
12 | Processor C | DS1 Slight | no | Lognormal | 1 | 0.75 | 0 | 0.28 | 0.03 | 0 | NA | null | null | Normal | 3 | 0.60796 | 1 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
13 | Processor C | DS2 Moderate | no | Lognormal | 1 | 1 | 0 | 0.3 | 0.15 | 0 | NA | null | null | Normal | 20 | 1.2159 | 2 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
14 | Processor C | DS3 Extensive | no | Lognormal | 1 | 1.33 | 0 | 0.34 | 0.4 | 0 | NA | null | null | Normal | 60 | 2.4318 | 4 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
15 | Processor C | DS4 Complete | no | Lognormal | 1 | 1.55 | 0 | 0.28 | 1.2 | 0 | NA | null | null | Normal | 102.8571 | 4.8637 | 8 | HAZUS-MH MR3 Table 8.22.a Generation Facilities
16 | Processor D | DS1 Slight | no | Lognormal | 1 | 0.28 | 0 | 0.25 | 0.05 | 1 | NA | null | null | Normal | 1 | 0.30398 | 0.5 | Not Available.
17 | Processor D | DS2 Moderate | no | Lognormal | 1 | 0.43 | 0 | 0.35 | 0.3 | 0 | NA | null | null | Normal | 3 | 0.91194 | 1.5 | Not Available.
18 | Processor D | DS3 Extensive | no | Lognormal | 1 | 0.6 | 0 | 0.4 | 0.75 | 0 | NA | null | null | Normal | 7 | 2.1278 | 3.5 | Not Available.
19 | Processor D | DS4 Complete | no | Lognormal | 1 | 0.85 | 0 | 0.4 | 1 | 0 | NA | null | null | Normal | 30 | 9.1194 | 15 | Not Available.
20 | Perturbator | DS1 Slight | no | Lognormal | 1 | 0.475 | 0 | 0.25 | 0.06 | 1 | NA | null | null | Normal | 5 | 0.30398 | 0.5 | Not Available.
21 | Perturbator | DS2 Moderate | no | Lognormal | 1 | 0.615 | 0 | 0.33 | 0.3 | 1 | NA | null | null | Normal | 17 | 0.60796 | 1 | Not Available.
22 | Perturbator | DS3 Extensive | no | Lognormal | 1 | 0.77 | 0 | 0.4 | 0.75 | 0 | NA | null | null | Normal | 37 | 1.2159 | 2 | Not Available.
23 | Perturbator | DS4 Complete | no | Lognormal | 1 | 1 | 0 | 0.4 | 1 | 0 | NA | null | null | Normal | 77.1429 | 2.4318 | 4 | Not Available.
24 | SYSTEM_OUTPUT | DS1 Slight | no | Lognormal | 1 | 10 | 0 | 0.01 | 0.01 | 1 | NA | null | null | Normal | 1 | 0.060796 | 0.1 | Not Available.
25 | SYSTEM_OUTPUT | DS2 Moderate | no | Lognormal | 1 | 10 | 0 | 0.01 | 0.01 | 1 | NA | null | null | Normal | 1 | 0.060796 | 0.1 | Not Available.
26 | SYSTEM_OUTPUT | DS3 Extensive | no | Lognormal | 1 | 10 | 0 | 0.01 | 0.01 | 1 | NA | null | null | Normal | 1 | 0.060796 | 0.1 | Not Available.
27 | SYSTEM_OUTPUT | DS4 Complete | no | Lognormal | 1 | 10 | 0 | 0.01 | 0.01 | 1 | NA | null | null | Normal | 1 | 0.060796 | 0.1 | Not Available.
28 | SYSTEM_INPUT | DS1 Slight | no | Lognormal | 1 | 10 | 0 | 0.01 | 0.01 | 1 | NA | null | null | Normal | 1 | 0.060796 | 0.1 | Not Available.
29 | SYSTEM_INPUT | DS2 Moderate | no | Lognormal | 1 | 10 | 0 | 0.01 | 0.01 | 1 | NA | null | null | Normal | 1 | 0.060796 | 0.1 | Not Available.
30 | SYSTEM_INPUT | DS3 Extensive | no | Lognormal | 1 | 10 | 0 | 0.01 | 0.01 | 1 | NA | null | null | Normal | 1 | 0.060796 | 0.1 | Not Available.
31 | SYSTEM_INPUT | DS4 Complete | no | Lognormal | 1 | 10 | 0 | 0.01 | 0.01 | 1 | NA | null | null | Normal | 1 | 0.060796 | 0.1 | Not Available.

## damage_state_def
component_type | damage_state | damage_state_definition
Processor A | DS1 Slight | Minor deformation to supporting structure with some yielding of hold-down bolts.
Processor A | DS2 Moderate | Significant deformaton to steel supporting structure with misaligment of ash handling conveyors
Processor A | DS3 Extensive | Horizontal displacement of structure with failure of bracing elements and damage to ash silo structure.
Processor A | DS4 Complete | Partial or complete collapse of ash handling system.
Processor B | DS1 Slight | Minor deformation to supporting structure and minor damage at lateral restraint points to boiler. No internal damage to boiler.
Processor B | DS2 Moderate | Significant deformation to supporting structure with deformation at holding down bolts and yielding of bracing elements. Damage to internal boiler pipes requiring access for repair.
Processor B | DS3 Extensive | Major damage to boiler support with failure of many bracing elements. Large deformations damage connecting pipework. Widespread damage to internal steam pipes in boiler requring extensive replacement.
Processor B | DS4 Complete | Damage beyond repair
Processor C | DS1 Slight | Minor deformations in connections or hairline cracks in a few welds. Minor brace deformation. Some deformation at hold down bolts.
Processor C | DS2 Moderate | Some steel members have yielded exhibiting observable permanent rotations at connections. A few welded connections may exhibit major cracks through welds or a few bolted connections may exhibit broken bolts or enlarged bolt holes. Some yielding of braces and soem anchor bolts stretched.
Processor C | DS3 Extensive | Many steel bracing elements have exceeded their yield capacity resulting in significant permanent lateral deformation of the structure. Many truss arch members have buckeld in compression. Some of the structural connections may have exceeded their ultimate capacity exhibited by major permanent member rotations at connections, buckled flanges and failed connections. Some foundation oviement due to settlement and some anchor bolts failed.
Processor C | DS4 Complete | A significant proportion of the structural elements have exceeded their ultimate capacities or some critical structural elements or connections have failed resulting in dangerous permanent lateral displacement, partial collapse or collapse of the shelter structure.
Processor D | DS1 Slight | Minor deformations in connections or hairline cracks in a few welds. Minor brace deformation. Some deformation at hold down bolts.
Processor D | DS2 Moderate | Some steel members have yielded exhibiting observable permanent rotations at connections. A few welded connections may exhibit major cracks through welds or a few bolted connections may exhibit broken bolts or enlarged bolt holes. Some yielding of braces and soem anchor bolts stretched.
Processor D | DS3 Extensive | Many steel bracing elements have exceeded their yield capacity resulting in significant permanent lateral deformation of the structure. Many truss arch members have buckeld in compression. Some of the structural connections may have exceeded their ultimate capacity exhibited by major permanent member rotations at connections, buckled flanges and failed connections. Some foundation oviement due to settlement and some anchor bolts failed.
Processor D | DS4 Complete | A significant proportion of the structural elements have exceeded their ultimate capacities or some critical structural elements or connections have failed resulting in dangerous permanent lateral displacement, partial collapse or collapse of the shelter structure.
Perturbator | DS1 Slight | Minor deformations in connections or hairline cracks in a few welds. Minor brace deformation. Minor spalling at some precast panel corners.
Perturbator | DS2 Moderate | Some steel members have yielded exhibiting observable permanent rotations at connections. A few welded connections may exhibit major cracks through welds or a few bolted connections may exhibit broken bolts or enlarged bolt holes. Some yielding of braces. More significant spalling damage to precast panels with deformation at panel connections.
Perturbator | DS3 Extensive | Most steel members have exceeded their yield capacity resulting in significant permanent lateral deformation of the structure. Some of the structural members or connections may have exceeded their ultimate capacity exhibited by major permanent member rotations at connections, buckled flanges and failed connections. Some anchor bolts stretched. Partial collapse of portions of the structure may have occurred due to failed critical elements or connections.
Perturbator | DS4 Complete | A significant proportion of the structural elements have exceeded their ultimate capacities or some critical structural elements or connections have failed resulting in dangerous permanent lateral displacement, partial collapse or collapse of the building.
SYSTEM_OUTPUT | DS1 Slight | not available
SYSTEM_OUTPUT | DS2 Moderate | not available
SYSTEM_OUTPUT | DS3 Extensive | not available
SYSTEM_OUTPUT | DS4 Complete | not available
SYSTEM_INPUT | DS1 Slight | not available
SYSTEM_INPUT | DS2 Moderate | not available
SYSTEM_INPUT | DS3 Extensive | not available
SYSTEM_INPUT | DS4 Complete | not available